LOADFLOW DOCUMENTATION

The program will allow you to solve a loadflow on a system up to 25 buses. You

can change the total load, the generator voltage schedules and the generator

MW schedules using the change option.

The loadflow program allows the user to run either a Gauss-Seidel or Newton

Raphson load flow algorithm, to change the data to set up specific cases and

to print out the input data and the solution data. There is also a feature to

allow the user to dump the solution voltages to a file so they may be read by

other programs.

PROGRAM DIMENSIONS

Max number of buses = 25

Max number of branches ( lines or transformers ) = 40

Max number of generator buses = 20

Max number of transformers = 10

A file giving the loadflow data for the the sixbus system shown in the text is

given in file SIXBUS.DAT. The format of the input file needed for the loadflow

program is as follows:

First and second lines are title lines of up to 80 characters each.

number of buses ( integer up to 30 )

number of generators

number of branches ( includes transformers and lines )

Busnumber of the swing bus

One line for each bus: Each field separated by one space.

bus number  bus name  p load  qload  volt high limit  volt low limit

Note: bus name can be eight characters maximum

one line for each generator:

bus number   p gen  scheduled voltage  q max  qmin

one line for each branch:

from bus number  to bus number  r  x  bcap   line flow limit  line type(see

below)

Note: bcap is one half of line's total charging

line type is either LINE or TRAN, if TRAN then follow on same line with

tap bus   non-tap bus   tap ratio

Here is a listing of file SIXBUS.DAT:

SIXBUS LOAD FLOW SAMPLE SYSTEM  <-- Title line 1

-----------------------------  <-- Title line 2

6  <-- Number of buses

3  <-- Number of generators

11  <-- Number of branches

1   <-- Bus number for swing bus

1 BUS-1    0.0 0.0 0.95 1.05  <-- Data for first bus

2 BUS-2    0.0 0.0 0.95 1.05

3 BUS-3    0.0 0.0 0.95 1.05

4 BUS-4    0.7 0.7 0.95 1.05

5 BUS-5    0.7 0.7 0.95 1.05

6 BUS-6    0.7 0.7 0.95 1.05

1 0.0 1.05 1.0 -1.0  <-- Data for first generator

2 0.5 1.05 1.0 -1.0

3 0.6 1.07 0.6 -1.0

1  2  0.10  0.20  0.02    1.0 LINE  <-- Data for first line

1  4  0.05  0.20  0.02    1.0 LINE

1  5  0.08  0.30  0.03    1.0 LINE

2  3  0.05  0.25  0.03    1.0 LINE

2  4  0.05  0.10  0.01    1.0 LINE

2  5  0.10  0.30  0.02    1.0 LINE

2  6  0.07  0.20  0.025   1.0 LINE

3  5  0.12  0.26  0.025   1.0 LINE

3  6  0.02  0.10  0.01    1.0 LINE

4  5  0.20  0.40  0.04    1.0 LINE

5  6  0.10  0.30  0.03    1.0 LINE

To run the load flow enter LOADFLOW. Program will ask for input data file and

then display menu of choices. See sample run below:

Enter name of input data file :SIXBUS.DAT <-- user enters input file name

Do you want output on printer? (Y or N) Y <-- user entered Y to send output

to the printer

Menu of options:

1 - print input data

2 - run Gauss-Seidel loadflow

3 - run Newton-Raphson loadflow

4 - print solution

5 - change input data

6 - write voltage solution to a file

7 - quit

Enter option >1 <-- user entered 1 to print out input data

###################################### This will appear on printer ###########

file: sixbus.dat

SIXBUS LOAD FLOW SAMPLE SYSTEM

-----------------------------

Number of Buses = 6

number of Lines = 11

Number of Generators = 3

Number of Transformers = 0

Swing Bus at bus number 1

Bus Data

Bus                                       Voltage     Voltage     Bus

Number  Bus Name   Mw Load    Mvar Load   High Limit  Low limit   Type

------  --------  ----------  ----------  ----------  ----------  -----

1  BUS_1     0.00000     0.00000     0.95000     1.05000  SWING

2  BUS_2     0.00000     0.00000     0.95000     1.05000  GEN

3  BUS_3     0.00000     0.00000     0.95000     1.05000  GEN

4  BUS_4    70.00000    70.00000     0.95000     1.05000  LOAD

5  BUS_5    70.00000    70.00000     0.95000     1.05000  LOAD

6  BUS_6    70.00000    70.00000     0.95000     1.05000  LOAD

Generator Data

Bus     Mw          Scheduled  High Mvar  Low MVar

number  Generation  Voltage    Limit      Limit

------  ----------  ---------  ---------  ---------

1     0.00000     1.0500     1.0000    -1.0000

2     0.50000     1.0500     1.0000    -1.0000

3     0.60000     1.0700     0.6000    -1.0000

Branch Data

From  To    Branch  Branch  Line      Branch     Branch  Tap   Non-Tap  Tap

Bus   Bus     R       X     Charging  Mva Limit  Type    Bus   Bus      Ratio

----  ----  ------  ------  --------  ---------  ------  ----  -------  ------

1     2  0.1000  0.2000  0.020000     1.0000    LIN

1     4  0.0500  0.2000  0.020000     1.0000    LIN

1     5  0.0800  0.3000  0.030000     1.0000    LIN

2     3  0.0500  0.2500  0.030000     1.0000    LIN

2     4  0.0500  0.1000  0.010000     1.0000    LIN

2     5  0.1000  0.3000  0.020000     1.0000    LIN

2     6  0.0700  0.2000  0.025000     1.0000    LIN

3     5  0.1200  0.2600  0.025000     1.0000    LIN

3     6  0.0200  0.1000  0.010000     1.0000    LIN

4     5  0.2000  0.4000  0.040000     1.0000    LIN

5     6  0.1000  0.3000  0.030000     1.0000    LIN

##############################################################################

Menu of options:

1 - print input data

2 - run Gauss-Seidel loadflow

3 - run Newton-Raphson loadflow

4 - print solution

5 - change input data

6 - write voltage solution to a file

7 - quit

Enter option >5 <-- user selects option to change input data

Change Input Data Options:

1 - change system load

2 - change generator scheduled voltage

3 - change generator scheduled MW

4 - Return to main menu

Enter option >1  <-- user selects 1 to change load

Present total system MW load =  210.00

Enter new total load MW: 180.0 <-- user enters 180.0 as new total load

Change Input Data Options:

1 - change system load

2 - change generator scheduled voltage

3 - change generator scheduled MW

4 - Return to main menu

Enter option > 2 <-- user enters 2 to select option to change gen voltages

Present generator voltages are :

Generator bus  1 PU sched voltage = 1.050

Generator bus  2 PU sched voltage = 1.050

Generator bus  3 PU sched voltage = 1.070

Enter generator bus number, a space, new PU scheduled voltage

(enter 0 0 to terminate ): 1 1.06 <-- user enters 1 to indicate gen on bus 1

and 1.06 as new gen voltage

Present generator voltages are :

Generator bus  1 PU sched voltage = 1.060 <-- new voltage now in input data

Generator bus  2 PU sched voltage = 1.050

Generator bus  3 PU sched voltage = 1.070

Enter generator bus number, a space, new PU scheduled voltage

(enter 0 0 to terminate ):0 0 <-- user enters 0 0 to escape from this option

Change Input Data Options:

1 - change system load

2 - change generator scheduled voltage

3 - change generator scheduled MW

4 - Return to main menu

Enter option > 3 <-- user enters 3 to select gen MW changes

Present generator MW schedules are :

Generator bus  1 scheduled MW =    0.00

Generator bus  2 scheduled MW =   50.00

Generator bus  3 scheduled MW =   60.00

Enter generator bus number, a space, new scheduled MW

(enter 0 0 to terminate ): 2 55.0 <-- user enters 2 to select gen bus 2 and

55.0 as new gen MW on bus 2.

Present generator MW schedules are :

Generator bus  1 scheduled MW =    0.00

Generator bus  2 scheduled MW =   55.00 <-- new gen schedule

Generator bus  3 scheduled MW =   60.00

Enter generator bus number, a space, new scheduled MW

(enter 0 0 to terminate ): 0 0 <-- user selects 0 0 to escape

Change Input Data Options:

1 - change system load

2 - change generator scheduled voltage

3 - change generator scheduled MW

4 - Return to main menu

Enter option >4 <-- user enters 4 to return to main menu

Menu of options:

1 - print input data

2 - run Gauss-Seidel loadflow

3 - run Newton-Raphson loadflow

4 - print solution

5 - change input data

6 - write voltage solution to a file

7 - quit

Enter option >3 <-- user selects 3 to run Newton load flow

**************************************************************

ITERATION 1

The maximum P mismatch is      0.3978

The maximum Q mismatch is      0.3608

**************************************************************

ITERATION 2

The maximum P mismatch is      0.0061

The maximum Q mismatch is      0.0126

**************************************************************

ITERATION 3

The maximum P mismatch is      0.0000

The maximum Q mismatch is      0.0000

Gen 3 at max var limit

**************************************************************

ITERATION 4

The maximum P mismatch is      0.0000

The maximum Q mismatch is      0.1196

**************************************************************

ITERATION 5

The maximum P mismatch is      0.0002

The maximum Q mismatch is      0.0012

**************************************************************

ITERATION 6

The maximum P mismatch is      0.0000

The maximum Q mismatch is      0.0000

Menu of options:

1 - print input data

2 - run Gauss-Seidel loadflow

3 - run Newton-Raphson loadflow

4 - print solution

5 - change input data

6 - write voltage solution to a file

7 - quit

Enter option >4 <-- user selects printout of solution

###################################### This will appear on printer ###########

Load Flow Solution:

file: sixbus.dat

SIXBUS LOAD FLOW SAMPLE SYSTEM

-----------------------------

From Volt.  Volt.   Mw      Mvar     Mw     Mvar   To    Mw      Mvar    Mva

Bus  Mag.   Angle   Load    Load     Gen.   Gen.   Bus   Flow    Flow    Flow

---- ------ ------ ------- ------- ------- ------- ---- ------- ------- -------

1 1.0600  0.000    0.00    0.00   69.74   30.47

2   15.03   -4.23   15.62

4   30.15   21.67   37.13

5   24.56   13.04   27.81

2 1.0500 -1.650    0.00    0.00   55.00   49.57

1  -14.83    0.19   14.83

3   -0.38   -7.08    7.09

4   34.43   32.54   47.38

5   14.61   11.74   18.74

6   21.17   12.18   24.42

3 1.0592 -1.698    0.00    0.00   60.00   60.00

2    0.39    0.44    0.59

5   19.02   14.04   23.64

6   40.59   45.52   60.99

4 1.0017 -2.609   60.00   60.00

1  -29.49  -23.28   37.57

2  -33.38  -32.55   46.62

5    2.87   -4.17    5.06

5 0.9967 -3.286   60.00   60.00

1  -23.94  -17.06   29.40

2  -14.24  -14.82   20.55

3  -18.33  -17.83   25.57

4   -2.85   -3.79    4.74

6   -0.64   -6.50    6.53

6 1.0079 -3.377   60.00   60.00

2  -20.74  -16.26   26.36

3  -39.91  -44.25   59.59

5    0.66    0.51    0.83

Mw gen                 =  184.74

Mvar gen               =  140.05

Mw load                =  180.00

Mvar load              =  180.00

Total I2R Mw losses    =    4.74

Total I2X Mvar losses  =   14.81

Total charging Mvar    =   54.76

##############################################################################

Menu of options:

1 - print input data

2 - run Gauss-Seidel loadflow

3 - run Newton-Raphson loadflow

4 - print solution

5 - change input data

6 - write voltage solution to a file

7 - quit

Enter option >6  <-- user enters 6 to select output of solution

Enter name of solution data file :SOL6-1.DAT  <-- user enters solution file name

Menu of options:

1 - print input data

2 - run Gauss-Seidel loadflow

3 - run Newton-Raphson loadflow

4 - print solution

5 - change input data

6 - write voltage solution to a file

7 - quit

Enter option >7 <-- user quits