SE program Documentation

The state estimator program on the disk was written in Turbo Pascal by David

Anderson a student at the University of Minnesota. It uses the full least

squares Newton algorithm as described in the text. The exercizes you are to

run will show you some of the interesting problems that have to be dealt with

in running a state estimator.

The options are more or less self explanatory and appear as follows:

When the state estimator is first called it will ask the use for an input

file. This is the state estimator input file produced by the SCADA

program. The input files already on the disk are SE6-1.DAT and

SE6-2.DAT. If you look at the input data it looks like this:

SIXBUS LOAD FLOW SAMPLE SYSTEM

------------------------------

6 < -- number of buses in network

11 <--- number of branches

LINE    1    2 1.000000E-01 2.000000E-01 2.000000E-02 <-- network data

LINE    1    4 5.000000E-02 2.000000E-01 2.000000E-02

LINE    1    5 8.000000E-02 3.000000E-01 3.000000E-02

LINE    2    3 5.000000E-02 2.500000E-01 3.000000E-02

LINE    2    4 5.000000E-02 1.000000E-01 1.000000E-02

LINE    2    5 1.000000E-01 3.000000E-01 2.000000E-02

LINE    2    6 7.000000E-02 2.000000E-01 2.500000E-02

LINE    3    5 1.200000E-01 2.600000E-01 2.500000E-02

LINE    3    6 2.000000E-02 1.000000E-01 1.000000E-02

LINE    4    5 2.000000E-01 4.000000E-01 4.000000E-02

LINE    5    6 1.000000E-01 3.000000E-01 3.000000E-02

V    1     1.0500000000E+00 1.0000E-04 <-- Voltage measurement

A    1     0.0000000000E+00 1.0000E-04 <-- Angle measurement

I    1     1.0787184632E+00 1.0000E-02     2.0661845009E-01 1.0000E-02 <Note 1

I    2     4.9999997662E-01 1.0000E-02     1.0000000977E+00 1.0000E-02

I    3     5.9999998886E-01 1.0000E-02     5.9999999981E-01 1.0000E-02

I    4    -6.9999998096E-01 1.0000E-02    -7.0000000156E-01 1.0000E-02

I    5    -6.9999998544E-01 1.0000E-02    -6.9999999870E-01 1.0000E-02

I    6    -6.9999998572E-01 1.0000E-02    -6.9999999611E-01 1.0000E-02

F    1     2  2.8692958226E-01 1.0000E-02 -1.5370907927E-01 1.0000E-02<Note 2

F    1     4  4.3642327195E-01 1.0000E-02  2.0994987978E-01 1.0000E-02

F    1     5  3.5536560904E-01 1.0000E-02  1.5037764958E-01 1.0000E-02

F    2     1 -2.7788988173E-01 1.0000E-02  1.2769252902E-01 1.0000E-02

F    2     3  1.6235984680E-02 1.0000E-02 -6.8377435238E-03 1.0000E-02

F    2     4  3.3625310382E-01 1.0000E-02  4.7475533519E-01 1.0000E-02

F    2     5  1.5913964961E-01 1.0000E-02  1.9011396619E-01 1.0000E-02

F    2     6  2.6626112024E-01 1.0000E-02  2.1427601078E-01 1.0000E-02

F    3     2 -1.6192816564E-02 1.0000E-02 -5.8643777671E-02 1.0000E-02

F    3     5  1.8031588029E-01 1.0000E-02  1.6516547801E-01 1.0000E-02

F    3     6  4.3587692513E-01 1.0000E-02  4.9347829947E-01 1.0000E-02

F    4     1 -4.2534439591E-01 1.0000E-02 -2.0719387096E-01 1.0000E-02

F    4     2 -3.2042041363E-01 1.0000E-02 -4.6386767810E-01 1.0000E-02

F    4     5  4.5764828576E-02 1.0000E-02 -2.8938452504E-02 1.0000E-02

F    5     1 -3.4376001515E-01 1.0000E-02 -1.6841831211E-01 1.0000E-02

F    5     2 -1.5275868126E-01 1.0000E-02 -2.1200810555E-01 1.0000E-02

F    5     3 -1.7264611277E-01 1.0000E-02 -1.9947687706E-01 1.0000E-02

F    5     4 -4.5314578737E-02 1.0000E-02 -4.7162224570E-02 1.0000E-02

F    5     6  1.4479402489E-02 1.0000E-02 -7.2934479408E-02 1.0000E-02

F    6     2 -2.5804510998E-01 1.0000E-02 -2.4269807516E-01 1.0000E-02

F    6     3 -4.2770560888E-01 1.0000E-02 -4.7323343926E-01 1.0000E-02

F    6     5 -1.4249266862E-02 1.0000E-02  1.5931518316E-02 1.0000E-02

Q

Note 1: This is an injection measurement: It consists of an identifier I

followed by the bus number followed by a puMW meas value , the standard

deviation ( sigma ) for the puMW meas, a puMVAR meas value and last of all the

standard deviation for the puMVAR value.

Note 2: This is a line flow measurement and consists of the identifier F

followed by the line from and to bus numbers ( the sense of the measurement is

to be taken as the flow going from the from bus to the to bus ). This is

followed by the puMW meas value, puMW sigma, puMVAR meas value and the sigma

for the puMVAR meas.

Options:

option 1 : Should only be called if you desire to go to another case.

option 2 : Will print out the input data currently loaded

option 3 : Can be used to remove or change a measurement value.

To remove a voltage measurement enter V space and its bus number and

hit enter. To remove an injection measurement enter I a space and its bus

number and hit enter. To remove a flow measurement enter F, a space, the from

bus number, a space, the to bus number and hit enter.

To change a measurement you must reenter the measurement line

as shown above. That is you enter the identifier, one or two bus numbers, the

puKV or MW meas value, sigma, MVAR and sigma.

option 4 : Uses a pseudo random noise generator to add noise to the

measurement values.

option 5: Printing the measurement values shows the input measurement values

and the values after adding noise.

option 6 : Runs the state estimator solution. NOTE the value of J as the

solution proceeds.

option 7 : The solution printout shows the injections and flows as calculated

from the voltages and angles estimated from the measurements.

option 8 : Calculates the individual residuals divided by the sigma of the

measurement itself.

option 9 : Calculates the normalized residual. This is the residual or error

between the measured value and the value calculated from the state estimator

divided by the sigma of the estimated value. See text. This is the sigma to

be used in identifying bad measurements.

option 10: Prints the residuals.

option 11: Quit.

Here is a sample run with the state estimator.

To run the state estimator you simply type SE and hit enter:

Enter name of state estimator data file :SE6-1.DAT  <-- User enters input file

name

Do you want output on printer? (Y or N) Y  <-- Output to printer

Menu of options:

1 - Read in a new input data file

2 - Print input data

3 - Edit measurement data

4 - Add noise to measurements

5 - Print measurement data

6 - Run State Estimator

7 - Print solution

8 - Calculate the weighted residuals

9 - Calculate the normalized residuals

10 - Print the residuals

11 - Quit

Enter option >4  <-- User enters 4 to add random noise to measured values

Menu of options:

1 - Read in a new input data file

2 - Print input data

3 - Edit measurement data

4 - Add noise to measurements

5 - Print measurement data

6 - Run State Estimator

7 - Print solution

8 - Calculate the weighted residuals

9 - Calculate the normalized residuals

10 - Print the residuals

11 - Quit

Enter option >3 <-- User enters 3 to edit measured values

Enter option type (V,A,I,F or Q use caps only), bus number(s),

measurement value(s), sigma(s)

V bus-number per-unit-voltage sigma

A bus-number phaseangle(in radians) sigma

I bus-number MW Psigma MVAR Qsigma

F fbus-number tbus-number MW Psigma MVAR Qsigma

Q to quit

Enter new measurement data ( or Q to quit) :

I 4 -75. .01 -75. .01 <-- User indicates that Injection measurement on bus 4

is to be set to -75MW and -75MVAR with sigmas = 0.01

Enter option type (V,A,I,F or Q use caps only), bus number(s),

measurement value(s), sigma(s)

V bus-number per-unit-voltage sigma

A bus-number phaseangle(in radians) sigma

I bus-number MW Psigma MVAR Qsigma

F fbus-number tbus-number MW Psigma MVAR Qsigma

Q to quit

Enter new measurement data ( or Q to quit) :

Q  <--User quits editing measurements

Menu of options:

1 - Read in a new input data file

2 - Print input data

3 - Edit measurement data

4 - Add noise to measurements

5 - Print measurement data

6 - Run State Estimator

7 - Print solution

8 - Calculate the weighted residuals

9 - Calculate the normalized residuals

10 - Print the residuals

11 - Quit

Enter option >5  <-- User enters 5 to print measurement data

######################## The following appears on the printer #################

File: se6-1.dat

SIXBUS LOAD FLOW SAMPLE SYSTEM

------------------------------

Number of Voltage Magnitude Measurements = 1

Number of Voltage Angle Measurements = 1

Number of Injection Measurements = 6

Number of Flow Measurements = 22

Bus Voltage Magnitude Measurements

Voltage Magnitude (in pu)

-------------------------------

Bus     With out     With     Standard

Number  Noise        Noise    Deviation

------  ---------  ---------  ---------

1    1.05000    1.04999    0.00010  <-- Note "with noise" value

Bus Voltage Angle Measurements

Voltage Angle in

Per Unit (i.e. Radians)

-------------------------------

Bus     With out    With      Standard

Number  Noise       Noise     Deviation

------  ---------  ---------  ---------

1    0.00000   -0.00003    0.00010

Bus Injection Measurements

Mw Injection                    Mvar Injection

-------------------------------  -------------------------------

Bus     With out     With     Standard   With out     With     Standard

Number  Noise        Noise    Deviation  Noise        Noise    Deviation

------  ---------  ---------  ---------  ---------  ---------  ---------

1    107.872    108.155      1.000     20.662     20.933      1.000

2     50.000     49.944      1.000    100.000     98.535      1.000

3     60.000     60.359      1.000     60.000     61.013      1.000

4    -75.000     NA          1.000    -75.000     NA          1.000 <--1

5    -70.000    -68.636      1.000    -70.000    -70.400      1.000

6    -70.000    -69.885      1.000    -70.000    -69.640      1.000

Branch Flow Measurements

Mw Flow                         Mvar Flow

-------------------------------  -------------------------------

From  To    With out     With     Standard   With out     With     Standard

Bus   Bus   Noise        Noise    Deviation  Noise        Noise    Deviation

----  ----  ---------  ---------  ---------  ---------  ---------  ---------

1     2     28.693     27.713      1.000    -15.371    -16.600      1.000

1     4     43.642     42.269      1.000     20.995     21.288      1.000

1     5     35.537     35.059      1.000     15.038     17.309      1.000

2     1    -27.789    -27.054      1.000     12.769     12.538      1.000

2     3      1.624      0.919      1.000     -0.684     -0.862      1.000

2     4     33.625     32.599      1.000     47.476     46.202      1.000

2     5     15.914     14.448      1.000     19.011     18.652      1.000

2     6     26.626     27.595      1.000     21.428     22.362      1.000

3     2     -1.619     -2.029      1.000     -5.864     -5.807      1.000

3     5     18.032     16.561      1.000     16.517     16.121      1.000

3     6     43.588     43.769      1.000     49.348     48.253      1.000

4     1    -42.534    -42.286      1.000    -20.719    -21.085      1.000

4     2    -32.042    -31.250      1.000    -46.387    -47.797      1.000

4     5      4.576      4.564      1.000     -2.894     -3.142      1.000

5     1    -34.376    -34.725      1.000    -16.842    -18.162      1.000

5     2    -15.276    -16.037      1.000    -21.201    -20.502      1.000

5     3    -17.265    -17.548      1.000    -19.948    -20.270      1.000

5     4     -4.531     -3.244      1.000     -4.716     -5.954      1.000

5     6      1.448     -0.163      1.000     -7.293     -9.349      1.000

6     2    -25.805    -26.109      1.000    -24.270    -25.024      1.000

6     3    -42.771    -43.346      1.000    -47.323    -47.658      1.000

6     5     -1.425      1.086      1.000      1.593      0.446      1.000

Menu of options:

1 - Read in a new input data file

2 - Print input data

3 - Edit measurement data

4 - Add noise to measurements

5 - Print measurement data

6 - Run State Estimator

7 - Print solution

8 - Calculate the weighted residuals

9 - Calculate the normalized residuals

10 - Print the residuals

11 - Quit

Enter option >6 <-- User run state estimator

Building R inverse.

***********************************************************

ITERATION 1

Building H matrix.

Building H transpose R inverse H.

Building delta Z.

Calculating the residual J.

The residual J is 3.41E+05  <-- Watch this number

Building H transpose R inverse delta Z.

Calculating and storing the table of factors.

Using the table of factors to calculate delta V.

updating the bus voltages.

Maximum angle mismatch is -0.10318 at bus 6

Maximum magnitude mismatch is 0.04998 at bus 1

***********************************************************

ITERATION 2

Building H matrix.

Building H transpose R inverse H.

Building delta Z.

Calculating the residual J.

The residual J is 1.59E+02

Building H transpose R inverse delta Z.

Calculating and storing the table of factors.

Using the table of factors to calculate delta V.

Updating the bus voltages.

Maximum angle mismatch is 0.00469 at bus 6

Maximum magnitude mismatch is 0.00268 at bus 6

***********************************************************

ITERATION 3

Building H matrix.

Building H transpose R inverse H.

Building delta Z.

Calculating the residual J.

The residual J is 8.15E+01

Building H transpose R inverse delta Z.

Calculating and storing the table of factors.

Using the table of factors to calculate delta V.

Updating the bus voltages.

Maximum angle mismatch is -0.00001 at bus 6

Maximum magnitude mismatch is -0.00000 at bus 4

Building delta Z.

Calculating the residual J.

The final value of the residual J is 8.15E+01

Menu of options:

1 - Read in a new input data file

2 - Print input data

3 - Edit measurement data

4 - Add noise to measurements

5 - Print measurement data

6 - Run State Estimator

7 - Print solution

8 - Calculate the weighted residuals

9 - Calculate the normalized residuals

10 - Print the residuals

11 - Quit

Enter option >7  <-- User prints solution

######################## The following appears on the printer #################

State Estimator Solution:

file: se6-1.dat

SIXBUS LOAD FLOW SAMPLE SYSTEM

------------------------------

From Volt.  Volt.   Mw       Mvar    To    Mw      Mvar    Mva

Bus  Mag.   Angle   Injec.   Injec.  Bus   Flow    Flow    Flow

---- ------ ------ -------- -------- ---- ------- ------- -------

1 1.0500 -0.002  107.88   22.09

2   28.68  -15.05   32.39

4   43.99   22.04   49.20

5   35.20   15.11   38.31

2 1.0493 -3.655   50.18   99.73

1  -27.79   12.44   30.44

3    1.35   -1.07    1.72

4   34.73   48.49   59.64

5   15.61   18.89   24.50

6   26.28   20.99   33.63

3 1.0433 -3.774   60.37   60.63

2   -1.35   -5.48    5.64

5   18.01   16.72   24.58

6   43.70   49.39   65.95

4 0.9855 -4.206  -71.82  -72.01  <-- Notice that bad values have influenced

the results of the estimator

1  -42.85  -21.61   47.99

2  -33.06  -47.23   57.66

5    4.10   -3.17    5.18

5 0.9744 -5.098  -68.82  -70.13

1  -34.06  -16.97   38.05

2  -14.98  -21.11   25.89

3  -17.24  -20.14   26.51

4   -4.06   -4.44    6.02

6    1.52   -7.46    7.61

6 0.9871 -5.644  -69.86  -69.49

2  -25.48  -23.90   34.93

3  -42.88  -47.35   63.89

5   -1.49    1.76    2.31

Mw losses   =    7.93

Mvar Losses =  -29.17

Menu of options:

1 - Read in a new input data file

2 - Print input data

3 - Edit measurement data

4 - Add noise to measurements

5 - Print measurement data

6 - Run State Estimator

7 - Print solution

8 - Calculate the weighted residuals

9 - Calculate the normalized residuals

10 - Print the residuals

11 - Quit

Enter option >9  <-- User runs normalized residual calculation

Building R inverse.

Building H matrix.

Building H transpose R inverse H.

Calculating and storing the table of factors.

Using the table of factors, H and R inverse to calculate D inverse.

Building delta Z.

Menu of options:

1 - Read in a new input data file

2 - Print input data

3 - Edit measurement data

4 - Add noise to measurements

5 - Print measurement data

6 - Run State Estimator

7 - Print solution

8 - Calculate the weighted residuals

9 - Calculate the normalized residuals

10 - Print the residuals

11 - Quit

Enter option >10  <--User prints normalized residuals

######################## The following appears on the printer #################

File: se6-1.dat

SIXBUS LOAD FLOW SAMPLE SYSTEM

------------------------------

Number of Voltage Magnitude Measurements = 1

Number of Voltage Angle Measurements = 1

Number of Injection Measurements = 6

Number of Flow Measurements = 22

Bus Voltage Magnitude Measurements

Voltage Magnitude (in pu)

--------------------------------

Bus     With out     With     Normalized

Number  Noise        Noise    Residual

------  ---------  ---------  ----------

1    1.05000    1.04999     -2.8892

Bus Voltage Angle Measurements

Voltage Angle in

Per Unit (i.e. Radians)

--------------------------------

Bus     With out    With      Normalized

Number  Noise       Noise     Residual

------  ---------  ---------  ----------

1    0.00000   -0.00003      0.0000

Bus Injection Measurements

Mw Injection                    Mvar Injection

--------------------------------  -------------------------------

Bus     With out     With     Normalized  With out     With     Normalized

Number  Noise        Noise    Residual    Noise        Noise    Residual

------  ---------  ---------  ----------  ---------  ---------  ---------

1    107.872    108.155      0.4008     20.662     20.933     -1.7147

2     50.000     49.944     -0.3831    100.000     98.535     -1.9786

3     60.000     60.359     -0.0096     60.000     61.013      0.5452

4    -75.000     NA         -4.3745    -75.000     NA         -4.0604

5    -70.000    -68.636      0.2961    -70.000    -70.400     -0.4256

6    -70.000    -69.885     -0.0387    -70.000    -69.640     -0.2081

Branch Flow Measurements

Mw Flow                          Mvar Flow

--------------------------------  --------------------------------

From  To    With out     With     Normalized  With out     With     Normalized

Bus   Bus   Noise        Noise    Residual    Noise        Noise    Residual

----  ----  ---------  ---------  ----------  ---------  ---------  ----------

1     2     28.693     27.713     -1.0127    -15.371    -16.600     -1.6102

1     4     43.642     42.269     -1.8078     20.995     21.288     -0.7927

1     5     35.537     35.059     -0.1504     15.038     17.309      2.2873

2     1    -27.789    -27.054      0.7611     12.769     12.538      0.1053

2     3      1.624      0.919     -0.4474     -0.684     -0.862      0.2184

2     4     33.625     32.599     -2.3474     47.476     46.202     -2.5358

2     5     15.914     14.448     -1.1835     19.011     18.652     -0.2425

2     6     26.626     27.595      1.3846     21.428     22.362      1.4520

3     2     -1.619     -2.029     -0.7075     -5.864     -5.807     -0.3377

3     5     18.032     16.561     -1.4954     16.517     16.121     -0.6246

3     6     43.588     43.769      0.0727     49.348     48.253     -1.2511

4     1    -42.534    -42.286      0.5874    -20.719    -21.085      0.5477

4     2    -32.042    -31.250      1.9861    -46.387    -47.797     -0.6149

4     5      4.576      4.564      0.4745     -2.894     -3.142      0.0260

5     1    -34.376    -34.725     -0.6854    -16.842    -18.162     -1.2304

5     2    -15.276    -16.037     -1.0725    -21.201    -20.502      0.6225

5     3    -17.265    -17.548     -0.3216    -19.948    -20.270     -0.1314

5     4     -4.531     -3.244      0.8270     -4.716     -5.954     -1.5298

5     6      1.448     -0.163     -1.7197     -7.293     -9.349     -1.9349

6     2    -25.805    -26.109     -0.6582    -24.270    -25.024     -1.1774

6     3    -42.771    -43.346     -0.5038    -47.323    -47.658     -0.3299

6     5     -1.425      1.086      2.6383      1.593      0.446     -1.3499

Menu of options:

1 - Read in a new input data file

2 - Print input data

3 - Edit measurement data

4 - Add noise to measurements

5 - Print measurement data

6 - Run State Estimator

7 - Print solution

8 - Calculate the weighted residuals

9 - Calculate the normalized residuals

10 - Print the residuals

11 - Quit

Enter option >11 <-- User quits