SCADA Documentation

The SCADA program simulates the functions performed by an on

line Supervisory Control And Data Acquision system. The idea is to

simulate the power system network, calculate all the voltages, P and

Q flows, P and Q injections, etc. on the system and then associate

these quantities with a specification of where measurements are

being made on the system.

The power system network is simulated by reading into SCADA the

same network data file read into the loadflow program. This file

specifies the network topology and the impedances of the branches.

The net P and Q injection specifications on the file are not used

by SCADA. You also need to read in the voltage solution file

produced by the loadflow. By specifying the voltage at each bus

SCADA can calculate the net injection at each bus as well as the

power flowing at each end of each branch of the network.

To complete the SCADA simulation we need a file that specifies

where each measurement is located and how good that measurement is

considered as reflected by specifying its standard deviation

(sigma). This data is captured in a measurement description data

file that looks like the file below: (see file MEAS6-1.DAT on you disk).

SIXBUS LOAD FLOW SAMPLE SYSTEM <-- Title line1

------------------------------ <-- Title line2

V    1   0.0001          < Bus voltage magnitude meas ( V Bus no. sigma )

A    1   0.0001          < Bus angle measurement ( A Bus no. sigma )

I    1   0.01   0.01     < Bus P+jQ injection meas ( I Bus No. Psigma Qsigma)

I    2   0.01   0.01

I    3   0.01   0.01

I    4   0.01   0.01

I    5   0.01   0.01

I    6   0.01   0.01

F    1   2  0.01  0.01  < Branch P+jQ flow meas ( F Fbus  Tbus Psigma  Qsigma)

F    1   4  0.01  0.01

F    1   5  0.01  0.01

F    2   1  0.01  0.01

F    2   3  0.01  0.01

F    2   4  0.01  0.01

F    2   5  0.01  0.01

F    2   6  0.01  0.01

F    3   2  0.01  0.01

F    3   5  0.01  0.01

F    3   6  0.01  0.01

F    4   1  0.01  0.01

F    4   2  0.01  0.01

F    4   5  0.01  0.01

F    5   1  0.01  0.01

F    5   2  0.01  0.01

F    5   3  0.01  0.01

F    5   4  0.01  0.01

F    5   6  0.01  0.01

F    6   2  0.01  0.01

F    6   3  0.01  0.01

F    6   5  0.01  0.01

Q    < End of measurements delimiter

The user must tell SCADA the name of the measurement description data

file so it can be read in. The SCADA program now has all necessary

information to produce the state estimator input file. This file

contains the network topology, impedances and measurement

information sufficient to run the state estimator. The measurement

data in the state estimator input file has the measurement location

in the network along with the measured value from that location and

the measurement's sigma values. The user must specify the name given

to the state estimator input file.

A sample run of SCADA is shown below:

From the operating system user enters SCADA and hits ENTER. The user then has

to enter four file name as described above:

Enter name of load flow data file :SIXBUS.DAT  <-- User entered loadflow data

file name

Enter name of solution data file :SOL6-1.DAT <-- User entered file name for

loadflow solution voltages

Enter name of measurement data file :MEAS6-1.DAT <-- User entered file name

for measurements data.

Enter name of state estimator data file :SE6-1.DAT <-- User entered name of

file on which SCADA

writes input data for

state estimator.

NOTE that the measured values in the state estimator input file

are "perfect" values, that is, they equal exactly the voltages,

injections and flow values that the load flow calculated. If You run

the state estimator on these values directly you should be able to

drive the state estimator's residual to virtually zero. However, a

real SCADA system will not have perfect measured values. Most of the

measured values will be in error by a slight amount ( corresponding

to random noise effects, transducer error, etc. ). Some of the

measurements will be in error by a large amount and we refer to

these as "bad" measurements.

The measurement errors can be simulated in two ways. Small

random errors can be added to the measurements in the state

estimator itself ( see SE.DOC ) using a psuedo random noise

generator that produces an error proportional to the measurement's

sigma. Large random errors can be simulated by outright changes to

the measured values either by editing the state estimator input data

file or using the editing functions in the SE program itself.

An interesting exercise for you students is to run the loadflow

program and SCADA program and then edit the state estimator input

data program and ask the students to "find" the bad data using the

normalized residual calculation.