UNIT COMMITMENT DOCUMENTATION

This documentation file describes the unit commitment program contained

in files UNITCOM.PAS and the executable file UNITCOM.EXE. The user

specifies several units and their associated data that are important to

running a unit commitment solution as well as a load curve to be met by those

units. The options specified at run time allow the user to choose the type of

unit list ( priority list or complete enumeration ) as well as parameters

associated with the dynamic programming solution.

***FILES

UNITCOM.DOC   This file

UNITCOM.PAS   PASCAL source file

UNITCOM.EXE   PASCAL executable file

UNITCOM0.DAT  Debug test case

UNITCOM1.DAT  Matches example 5E in chapter five of the text

UNITCOM2.DAT  An eight unit test system ( good to show program run time

differences between priority and enumeration)

UNITCOM.EXR   Student exercizes with unit commitment

***GENERATION UNIT DATA

The generating unit heat rate curve is represented as a single straight line

segment curve as shown chapter five of the text. Therefore only the unit's

low limit, high limit, incremental cost, and no load cost are input. The

start up cost and fuel cost are also included together with such parameters as

minimum down and up time and the initial unit status.

***LOAD CURVE DATA

The load curve is specified as a series of constant MW load periods.

Each load period may be any length in hours as set by the user.

Up to 8 periods of load data may be input.

***INPUT DATA FILE FORMAT

The unit commitment input data file starts with two header lines of up to 80

characters each.

This is followed by a line with a single number equal to the number of

generating units represented.

Each generating unit has exactly four lines of data. The first is a dummy line

of characters much like the header ( it is ignored by the program and just

serves as a label in the data file). The second line contains the unit low

limit in MW, the unit high limit in MW and the unit incremental heat rate in

Btu/k Wh. The third line contains the unit no load cost in R/h , the

unit start up cost in R and the unit fuel cost in R/MBtu. The fourth

line contains three integers: the unit minimum up time in hours, the

unit minimum down time in hours and the initial unit status in hours

(positive being hours up and negative being hours down at the start of

the schedule).

This is followed by another line with two entries containing the number

of periods in the load schedule and the length in hours for each period.

This is followed by a line with MW load values one for each period in

the schedule.

Example:

This example is for file UNITCOM1.DAT on your disk. The arrow <---- will

denote comments and is not on the file.

UNIT COMMITMENT DATA FILE - 8 PERIODS/4 UNITS ( Chapter 5 example )

-----------------------------------------------------------------

4                    <---- number of units

unit 1 data          <---- dummy "comment line for first unit

25.0  80.0  10440.0  <---- unit 1 min MW, max MW, inc heat rate.

213.0  350.0  2.0    <---- unit 1 no load cost, start up cost, fuelcost

4  2  -5             <---- unit 1 min up time, min down time, initial status

unit 2 data          <---- dummy line for second unit

60.0  250.0  9000.0

585.62 400.0  2.0

5  3  8

unit 3 data

75.0  300.0  8730.0

684.74 1100.0  2.0

5  4  8

unit 4 data

20.0  60.0  11900.0

252.0  0.02 2.0

1  1  -6

8  1.0                   <---- number of periods and length period in hours

450.0  530.0  600.0  540.0  400.0  280.0  290.0  500.0 <---- load MW values

***PROGRAM MAXIMUM DIMENSIONS

Maximum number of units = 10

Maximum numbers of periods in the schedule = 8

Maximum number of states in dynamic programming search = 256

***USER OPTIONS

The user is first asked to enter the name of the unit commitment data file.

Next the user is asked to select priority order or complete enumeration for

the solution. NOTE there is only enough storage allocated for 256 states in the

dynamic programming search routine. This means that up to an eight unit problem

can have complete enumeration. For more than eight units you are limited to

priority order.

Next the user is asked for the number of search states in the previous period

( parameter N in figure 5.6 of text ) and the present period ( parameter X in

fig 5.6 ). These have a great influence on solution speed and whether a

solution may be reached or not.

Finally, the user has the option of including or not including minimum up and

down constraints.

***SAMPLE PROGRAM EXECUTION

UNITCOM  <---- user starts unitcom program

DO YOU WANT OUTPUT ON THE PRINTER? (Y OR N): N <--- user selects crt output

ENTER NAME OF INPUT FILE :  UNITCOM1.DAT  <---- user enters data file name

SELECT UNIT ORDER OPTION

1 - PRIORITY ORDER

2 - COMPLETE ENUMERATION

ENTER OPTION NUMBER 1  <---- user picks option 1, priority order

ENTER NUMBER OF SEARCH STATES IN PREVIOUS PERIOD (N) ? 4  <---- user sets N=4

ENTER NUMBER OF SEARCH STATES IN PRESENT PERIOD (X) ? 4   <---- user sets X=4

INCLUDE UP/DOWN TIME CONSTRAINTS (Y OR N) :? Y  <---- includes up/down

constraints

######################### the following appears on the printer ###############

DATA FILE : unitcom1.dat

UNIT COMMITMENT DATA FILE - 8 PERIODS/4 UNITS ( Chapter 5 example )

-----------------------------------------------------------------

UNIT DATA

UNIT  MIN  MAX   INC   NO LOAD START  FUEL  MIN UP MIN DOWN  INIT

MW   MW    COST   COST    COST  COST   HRS    HRS      STATUS

1   25   80  10440    213     350    2      4      2        -5

2   60  250   9000    586     400    2      5      3         8

3   75  300   8730    685    1100    2      5      4         8

4   20   60  11900    252       0    2      1      1        -6

LOAD DATA DURING PERIODS OF 1.000 HOURS

PERIOD   LOAD

MW

1      450.000

2      530.000

3      600.000

4      540.000

5      400.000

6      280.000

7      290.000

8      500.000

PRIORITY ORDER

NUMBER OF SEARCH STATES PREVIOUS PERIOD = 4

NUMBER OF SEARCH STATES PRESENT PERIOD = 4

MIN UP/DOWN CONSTRAINTS ARE INCLUDED

UNIT STATUS TABLE USED IN DYNAMIC PROGRAMMING SEARCH

STATE  UNIT STATUS

1   2   3   4

-----------------------

1    OFF OFF ON  OFF

2    OFF ON  ON  OFF                <----- priority order state table

3    ON  ON  ON  OFF

4    ON  ON  ON  ON

INITIAL CONDITIONS

STATE  UNIT STATUS       PCOST  PATH    FCOST

1   2   3   4     R/HR            R

----------------------------------------------

2    -5   8   8  -6        0.    0   0          <---- initial conditions

PERIOD  1    SYSTEM LOAD  450

STATE  UNIT STATUS       PCOST  PATH    FCOST

1   2   3   4     R/HR            R

----------------------------------------------

2    -6   9   9  -7     9208    2   9208.361

3     1   9   9  -7     9493    2   9843.361          <---- period 1 paths

4     1   9   9   1     9861    2   10211.38

PERIOD  2    SYSTEM LOAD  530

STATE  UNIT STATUS       PCOST  PATH    FCOST

1   2   3   4     R/HR            R

----------------------------------------------

2    -7  10  10  -8    10648    2   19856.72

3     1  10  10  -8    10933    2   20491.72           <---- period 2 paths

4     1  10  10   1    11301    2   20859.74

PERIOD  3    SYSTEM LOAD  600

STATE  UNIT STATUS       PCOST  PATH    FCOST

1   2   3   4     R/HR            R

----------------------------------------------

3     1  11  11  -9    12265    2   32472.08

4     1  11  11   1    12576    2   32782.5

PERIOD  4    SYSTEM LOAD  540

STATE  UNIT STATUS       PCOST  PATH    FCOST

1   2   3   4     R/HR            R

----------------------------------------------

3     2  12  12 -10    11113    3   43585.44

4     2  12  12   1    11481    3   43953.46

PERIOD  5    SYSTEM LOAD  400

STATE  UNIT STATUS       PCOST  PATH    FCOST

1   2   3   4     R/HR            R

----------------------------------------------

3     3  13  13 -11     8593    3   52178.8

4     3  13  13   1     8964    3   52549.53

PERIOD  6    SYSTEM LOAD  280

STATE  UNIT STATUS       PCOST  PATH    FCOST

1   2   3   4     R/HR            R

----------------------------------------------

3     4  14  14 -12     6490    3   58668.86

4     4  14  14   1     6869    3   59047.68

PERIOD  7    SYSTEM LOAD  290

STATE  UNIT STATUS       PCOST  PATH    FCOST

1   2   3   4     R/HR            R

----------------------------------------------

3     5  15  15 -13     6665    3   65333.52

4     5  15  15   1     7043    3   65712.34

PERIOD  8    SYSTEM LOAD  500

STATE  UNIT STATUS       PCOST  PATH    FCOST

1   2   3   4     R/HR            R

----------------------------------------------

2    -1  16  16 -14    10108    3   75441.88

3     6  16  16 -14    10393    3   75726.88

4     6  16  16   1    10761    3   76094.9

OPTIMUM COMMITMENT SCHEDULE

TOTAL COST =  75441.88        <---- final optimum cost

PERIOD  STATE  UNIT STATUS       PCOST       LOAD

1   2   3   4      R/HR        MW

-------------------------------------------------

8      2    OFF ON  ON  OFF    10108      500.0

7      3    ON  ON  ON  OFF     6665      290.0

6      3    ON  ON  ON  OFF     6490      280.0

5      3    ON  ON  ON  OFF     8593      400.0         <---- final schedule

4      3    ON  ON  ON  OFF    11113      540.0

3      3    ON  ON  ON  OFF    12265      600.0

2      2    OFF ON  ON  OFF    10648      530.0

1      2    OFF ON  ON  OFF     9208      450.0

##############################################################################

DO YOU WANT TO RUN UNITCOM AGAIN? (Y OR N) :? N <---- user exits

See UNITCOM.EXR file for exercises for students.