Power System Application Data Dictionary

Version: 2.1

Date: July 1, 1995

- Analog Data

- Application Miscellaneous Data

- Bus Data

- Company Data

- Connectivity Node Data

- Equivalent AC Series Device Data

- Equivalent Injection/Shunt Device Data

- Generator Data

- - Generator Capability Curve Data

- - Generator Grouping Data

- - Generator Heat Rate Curve Data

- - Generator Output Allocation Data

- - Generator Rating Data

- Group Data

- Interchange Control Data

- Line Data

- - Line D.C. Data

- - Line Mutual Coupling Data

- Load Data

- - Load (Voltage Dependent Model) Data

- - Load (Voltage and Frequency Dependent Model) Data

- - Load (Tabular Definition of Power vs Voltage) Data

- - Load (Induction Motor Model) Data

- - Load (Generator Dependent Model) Data

- Ownership Data

- Rating Data

- Shunt (Nonsynchronous) Device Data

- Station Data

- Status Data

- Switching Device Data

- Transaction Data

- Transformer Data

- - Transformer Grouping Data

- - Transformer Winding

- - Transformer Manually Adjusted Tap Data

- - Transformer Winding Rating Data

- - Transformer TCUL Data

- - Transformer Maunally Adjusted Phase Shift Data

- - Transformer Automatically Adjusted Phase Shift Data

Analog Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Analog Number AnalogNumber | Unique number identifying the analog information |  |  |  | Integer |
| Analog Set number AnalogSet | Number identifying the set of analog values referenced by a device |  |  |  | Integer |
| Analog Name AnalogName | Name of analog information |  |  |  | Text |
| Analog value source AnalogSource | Source of analog value where: A = application solution T = telemetry P = pseudomeasurement S = schedule |  | Defaults to zero |  | Integer |
| Type AnalogType | Indicates what type this is, where: VM = Voltage Magnitude, Kv MW = Megawatts MR = Megavoltamperes- reactive MA = Megavoltamperes A = Amp TR = Transformer voltage Ratio TA = Tranformer Phase angle TT = Transformer Tap position VA = Voltage Angle, deg. FQ = Frequency |  |  | Mandatory | Text |
| Analog Assigned Device AnalogAssignDevice | Indicates device type which is associated with values, where: BS = Bus section LN = Line TR = Transformer SW = Switching device GN = Generator LD = Load SH = Shunt IA = Interchange Area |  |  |  | Text |
| Analog Location AnalogLocation | Indicates location of a measurement on devices where multiple locations exist (i.e., buses, lines, etc.), where location is the connectivity node number (ConnectivityNodeNumber) or bus number (BusNumber)of a measurement. |  |  | Bus Number or Connectivity Node number is provided based on setting of ModelConnectivityType | Integer |
| Analog Value AnalogValue | Numeric value |  |  | Sign convention of “flow” values is typically positve out of the bus section for series devices and into bus for shunt devices | Real |

Analog Data  (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Analog Sign Reversal AnalogSignRev | Indicates that the sign of the value should be reversed before being used at the location indicated due to available value opposite normal sign convention of AnalogValue, where, blank = no reversal - = reverse sign |  |  |  | Text |
| Analog Quality Code AnalogQuality | Indicates quality of value, where: G = Good B = Bad UA = Unavailable DV = Default Value OV = Override value |  | Defaults to G (Good) | Optional | Text |
| Analog Use Code AnalogUse | Indicates utilization instructions, where: U = Use if Good F = Forced Use (e.g., as external system reg. voltage or pseudomeasurement I = Inhibit Use |  |  | Optional | Text |
| Analog Standard Deviation AnalogStdDev | Indicates one standard assuming “bell” shaped curve (no bias) |  |  | Mandatory | Real |
| Analog Estimated Value AnalogEstValue | Numeric value of the estimated value |  |  | Optional | Real |
| Analog Normalized Residual AnalogNormResidual | Numeric value of estimated value divided by covariance |  |  | Optional | Real |
| Analog Estimated Value Quality Code AnalogEstQuality | Indicates quality of estimated value, where: G = Good S = Suspect TC = Telemetry Correction |  |  | Optional | Integer |

Application Miscellaneous Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Base MVA BaseMVA | MVA base for per unit derivation | MVA | 100. | Mandatory if non-p.u. information (Mw, Amps, etc.) provided | Real |
| Case title Title | User defined case title for data provided |  |  |  | Text |
| Model Connectivity Type ModelConnectivityType | Indicates what form bus model connectivity data is provided in: BM or BusModel BS or BusSection BO or Both |  | Defaults to BusModel | If BusSection, switching device data must exist to define bus sections. | Text |
| Post-Contingency Generator MW Response ContingencyGenMWResponse | Indicates method of assigning generator response to contingency, where: RF = Use gen. response factors PC = Proportional to gen Mw capacity PO = Proportional to gen Mw output AI = Per area interchange control |  |  | Mandatory if contingency cases defined | Text |

Buses

| Name | Definition | Units | Default | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Bus Identifier, BusNumber | Loadflow integer identifier,bus number |  |  | Mandatory; must be unique and > zero | Integer |
| Bus Name BusName | Loadflow character identifier,bus name |  |  | Mandatory; must be unique when used in combination with base voltage - BasekV | Text |
| Bus base voltage, BasekV | Base voltage line-to-line RMS if a.c. ; Line-to-ground if d.c. | kV |  | Mandatory; must be unique when used in combination with bus name -BusName | Real |
| Final Bus Island FinalBusIsland | Electrical island in which bus is loacated |  |  |  | Integer |
| Bus split indicator SplitBusIndicator | Number of primary bus (BusNumber) from which this bus was split. Informational |  |  | Used when ModelConnectivityType is BM (i.e.,bus model) since no topology process to resolve bus sections is assumed | Integer |
| Status BusStatus | Indicates whether the bus is in service or not; Out = out of service In = in service |  | Defaults to In |  | Text |
| Voltage Magnitude solved, BusVmagSolve | Magnitude of bus voltage. Solved value | per unit | Defaults to unity | Calculated by power flow or state estimation solution. This attribute may be used instead of BusAnalogSet for solution values. | Real |
| Phase Angle solved, BusVangleSolve | Phase angle of bus voltage; zero for d.c. bus. Solved value | degrees | defaults to zero | -360 < value < 360 Calculated by power flow or state estimation solution. This attribute may be used instead of BusAnalogSetNo for solution values. | Real |
| Bus MW Mismatch BusMWMismatch | Net Mw not assigned to generator, load or shunt (or est. Mw on zero injection bus) | MW |  |  | Real |
| Bus Mvar Mismatch BusMvarMismatch | Net Mvar not assigned to generator, load or shunt (or est. Mvar on zero injection bus) | Mvar |  |  | Real |
| Bus Analog set BusAnalogSetNo | Set number of analog measurement for bus voltages (AnalogSet) |  |  |  | Integer |

Buses (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Bus Observability BusObserv | Indication of bus observability from State Estimation, where: U = Unobservable O = Observable OB = Observable Boundary |  |  | Optional | Text |
| Bus Base Frequency BusBaseFreq | Bus base frequency; zero for d.c. bus | hertz | Defaults to system frequency |  | Real |
| Bus actual frequency BusActualFreq | Actual frequency at bus in per unit of bus base frequency; zero for d.c. bus | per unit | Defaults to unity |  | Real |
| Geographic Coordinate X BusCoordX | Approximate geographic location of the bus along a given horizontal axis | not specified |  |  | Real |
| Geographic Coordinate Y BusCoordY | Approximate geographic location of the bus along a given vertical axis | not specified |  |  | Real |
| Bus Location BusLocation | Group set (GroupSet) number to which this bus belongs |  |  | Optional if BusStationLocation not used for defining stations | Integer |
| Station Location BusStationLocation | Station location (StationNumber) where Bus is located |  |  | Optional. Should not be used if BusLocation used to define stations | Integer |
| Descriptive Text BusDescription | Text describing this bus |  |  |  | Text |
| Bus Type Code BusTypeCode | Type of Bus *L or Load (no control) *CB or ControlToBand (Lower Voltage Control Limits, Upper Voltage Control Limit) *CT or ControlToTarget -(Voltage target - within Controlling Element limits) *S = Swing (Bus Fixed Voltage and Angle) *I = Isolated (Bus electrically isolated) |  | Defaults to L or Load |  | Text |
| Voltage Target BusVoltTarget | Voltage magnitude setpoint | per unit |  | Mandatory if control objective code (BusTypeCode) is CT or S | Real |

Buses (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Lower Voltage Control Limit BusLowVoltLim | Voltage control band lower limit | per unit |  | Mandatory if BusTypeCode is CB | Real |
| Upper Voltage Control Limit BusUpVoltLim | Voltage control band upper limit | per unit |  | Mandatory if BusTypeCode is CB | Real |
| Bus volt limit ID (1...N) BusLimitId | Rating number assigned to limit (RatingNumber) |  |  |  | Integer |
| Bus Voltage limit Value (1...N) BusLimitValue | Rating Value for limit of this bus for corresponding Rating ID | As defined by rating units |  |  | Real |
| Control priority code BusControlPriorityCode | Character string containing letters T S N and C ordered left to right in Controlling Element priority T= transformer S= Synchronous machine N =nonsynchronous shunt reactive device C= d.c. converter |  |  | No leading blanks. Up to 4 characters long | Text |
| Commissioning Date BusCommission | Date the device goes into service | MM/DD/YY |  |  | Date |
| Decommissioning Date BusDecommission | Date the device goes out of service | MM/DD/YY |  |  | Date |
| Bus Ownership BusOwnershipSet | Owner of this bus (OwnershipSet number if not 100%, set = 0) |  | Default = 0 | Active attribute if 100 % ownership can be assumed, otherwise ownership set number | Integer |
| Negative Sequence Voltage BusNegSeqVolt | Magnitude of negative sequence voltage | per unit | Defaults to zero |  | Real |
| Negative Sequence Angle BusNegSeqAng | Phase angle of negative sequence voltage at this bus | degrees | Defaults to zero |  | Real |
| Zero Sequence Voltage BusZeroSeqVolt | Magnitude of zero sequence voltage | per unit | Defaults to zero |  | Real |
| Zero Sequence Angle BusZeroSeqAng | Phase angle of zero sequence voltage at this bus | degrees | Defaults to zero |  | Real |

Company Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Company Number CompanyNumber | Unique number identifying Company data |  |  | Mandatory, if this type data is used by Station (StationCompanyLocation). Use of Company object is optional if Group Object is used to group Station (StationLocation) | Integer |
| Company Name CompanyName | Name of Company |  |  | Optional | Text |

Connectivity Node

| Name | Description |  | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- | --- |
| Connectivity Node Number ConnectivityNodeNumber | Unique number identifying Connectivity Node where terminals of equipment connect through zero impedance connections |  |  |  | Mandatory, if this type data is used; Numbers used must be unique within a given bus | Integer |
| Connectivity Node Name ConnectivityNodeName | Name describing Connectivity Node |  |  |  | Optional | Text |
| Connectivity Node Analog Set ConnectivityNodeAnalogSetNo | Set number of analog for connectivity node voltages (AnalogSet) |  |  |  |  | Integer |
| Bus Location of Connectivity Node ConnectivityNodeBusNumber | Bus Number (BusNumber) at which Connectivity Node is located |  |  |  |  | Integer |

Equivalent AC Series Element Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Equivalent series element number EquivSeriesNumber | Unique number for the equivalent series element |  |  | Mandatory | Integer |
| Equivalent Series element Name EquivSeriesName | Name of equivalent series element |  |  | Mandatory | text |
| From Bus Identifier EquivSeriesFromBusNo | Number of "from" bus of this line branch |  |  | Mandatory; If From Bus Name is ommitted | Integer |
| From Bus Name EquivSeriesFromBusName | Name of “from” bus of this line branch |  |  | Mandatory If From Bus Indentifier is ommitted | Text |
| From Bus Section Number EquivSeriesFromNodeNo | Number of “from” connectivity node connection of this line |  |  | Required if ModelConnectivityType equal BS or BO | Text |
| To Bus Identifier EquivSeriesToBusNo | Number of "to" bus of this line |  |  | Mandatory; if EquivSeriesToBusName is omitted | Integer |
| To Bus Name EquivSeriesToBusName | Name of “to” bus of this line |  |  | Mandatory if EquivSeriesToBusNo is omitted |  |
| To Bus Section Number EquivSeriesToNodeNo | Number of “to” connectivity node connection of this line |  |  | Required if ModelConnectivityType equal BS or BO | Text |
| Circuit Identifier EquivSeriesCircuit | Alphanumeric circuit identifier to distinguish among several linesbranches joining the same pair of buses |  |  | Mandatory | Text |
| Equivalent series element Status EquivSeriesStatus | Identifies line’s status information in Status measurement data via StatusNumber entry |  | Defaults to unity | Primary use if ModelConnectivityType = BM model is used (i.e., bus model with no topology processing) | Integer |
| Equivalent Series element Analog Values Set EquivSeriesAnalogSetNo | Identifies the set of the line’s analog information in analog measurement data via AnalogSet |  |  |  | Integer |

Equivalent AC Series Element Data (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Equivalent series device From MW Flow solved, EquivSeriesFromMWSolve | Magnitude of equivalent series device MW flow at From end. Solved value | MW |  | Calculated by power flow or state estimation solution. This attribute may be used instead of EquivSeriesAnalogSetNo for solution values. Positive out of bus. | Real |
| Equivalent series device From Mvar Flow solved, EquivSeriesFromMvarSolve | Magnitude of Equivalent series device Mvar flow at From end. Solved value | Mvar |  | Calculated by power flow or state estimation solution. This attribute may be used instead of EquivSeriesAnalogSetNo for solution values. Positive out of bus. | Real |
| Equivalent series device To MW Flow solved, EquivSeriesToMWSolve | Magnitude of Equivalent series device MW flow at To end. Solved value | MW |  | Calculated by power flow or state estimation solution. This attribute may be used instead of EquivSeriesAnalogSetNo for solution values. Positive out of bus. | Real |
| Equivalent series device To Mvar Flow solved, EquivSeriesToMvarSolve | Magnitude of Equivalent series device Mvar flow at To end. Solved value | Mvar |  | Calculated by power flow or state estimation solution. This attribute may be used instead of EquivSeriesAnalogSetNo for solution values. Positive out of bus. | Real |

Equivalent AC Series Element Data (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Commissioning Date EquivSeriesCommission | Date the device goes into service | MM/DD/YY |  |  | Date |
| Decommissioning Date EquivSeriesDecommission | Date the device goes out of service | MM/DD/YY |  |  | Date |
| Equivalent Series Resistance, R EquivSeriesSectionR | Series resistance of this section | per unit on system base MVA and section base voltage |  | Mandatory | Real |
| Equivalent Series Reactance, X EquivSeriesSectionX | Series reactance of this section | per unit on system base MVA and section base voltage |  | Mandatory; for a d.c. line base frequency must be system frequency | Real |
| Shunt Conductance, +G EquivSeriesLineShuntCond | Total uniformly distributed shunt conductance of this series element | per unit on system base MVA and section base voltage | Defaults to zero |  | Real |
| Shunt Susceptance, +B EquivSeriesLineShuntSuscept | Total uniformly distributed shunt susceptance of this series element | per unit on system base MVA and section base voltage |  | Mandatory; for a d.c. line base frequency must be system frequency | Real |

Equivalent Injection/Shunt Element Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Equivalent inj/shunt element number EquivShuntNumber | Unique number for the equivalent inj/shunt element |  |  | Mandatory | Integer |
| Equivalent Inj/shunt element Name EquivShuntName | Name of equivalent inj/shunt element |  |  | Mandatory | text |
| Bus Identifier EquivShuntBusNo | Number of terminal bus (BusNumber) of this line branch |  |  | Mandatory; If From Bus Name is ommitted | Integer |
| Bus Name EquivShuntBusName | Name of terminal bus of this line branch |  |  | Mandatory If From Bus Indentifier is omitted | Text |
| Bus Section Number EquivShuntConnectivityNode | Number of terminal bus section connection of this line branch |  |  | Required if ModelConnectivityType not equal BM | Text |
| Commissioning Date EquivShuntCommission | Date the device goes into service | MM/DD/YY |  |  | Date |
| Decommissioning Date EquivShuntDecommission | Date the device goes out of service | MM/DD/YY |  |  | Date |
| Equivalent inj/status element Status EquivShuntStatus | Identifies shunt’s status information in Status measurement data via StatusNumber entry |  | Defaults to unity | Primary use if ModelConnectivityType = BM model is used (i.e., bus model with no topology processing) | Integer |
| Equivalent Inj/Shunt element Analog Values Set EquivShuntAnalogSetNo | Identifies the set of the shunt’s analog information in analog measurement data via AnalogSet if |  |  |  | Integer |
| Equivalent Injection/Shunt Type EquivShuntType | Type of equivalent device, where PQ = PQ Injection GB = Shunt GB Admittance |  |  | Mandatory | Integer |
| Equivalent Shunt Conductance, +G EquivShuntConductance | Total uniformly distributed shunt conductance of this series element if type = 1 | per unit on system base MVA and section base voltage | Defaults to zero |  | Real |
| Equivalent Shunt Susceptance, +B EquivShuntSusceptance | Total uniformly distributed shunt susceptance of this shunt element if type = 1 | per unit on system base MVA and section base voltage |  |  | Real |

Equivalent Injection/Shunt Element Data (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Equivalent Shunt MW solved, EquivShuntMWSolve | Magnitude of Equivalent Shunt MW. Solved value | MW |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of EquivShuntAnalogSetNo for solution values. Positive out of Bus. | Real |
| Equivalent Shunt Mvar solved, EquivShuntMvarSolve | Magnitude of Equivalent Shunt Mvar. Solved value | Mvar |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of EquivShuntAnalogSetNo for solution values. Positive out of Bus. | Real |

Generators

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Generator Number GeneratorNumber | Unique Number representing generator |  |  |  | integer |
| Generator Name GeneratorName | Unique Name for generator |  |  |  | text |
| Bus Identifier GeneratorBusNo | number of bus (BusNumber) to which machine is connected |  |  | mandatory | integer |
| Bus Section Identifier GeneratorConnectivitiyNode | Indicates connectivity node connection point of generator (ConnectivityNodeNumber) |  |  | Mandatory when ModelConnectivityType equal BS or BO | integer |
| Machine Identifier GeneratorUnitNumber | alphanumeric identifier to distinguish among multiple machines at this bus |  |  | Optional if Genertor number not provided; must uniquely identify the machine when used in conjunction with bus identifier | Text |
| Generator Status GeneratorElectricalStatus | Identifies generator’s status information in Status data via StatusNumber entry |  |  | Primary use if ModelConnectivityType = BM model is used (i.e., bus model with no topology processing) | Integer |
| Machine Base MVA GeneratorBaseMVA | MVA base used in expressing machine electrical parameters in per unit (may be system BaseMVA or machine base) | MVA |  | mandatory; > 0 | real |
| Machine Base Voltage GeneratorBasekV | voltage base used in expressing machine electrical parameters in per unit | kV |  | mandatory; > 0 | real |
| Committment Group Identifier GeneratorCommitmentGroupSet | Number of group GroupSet to which this unit is assigned to indicate the unit changes status on or off-line together with the other machines assigned to this group |  | defaults to zero |  | integer |
| Generator MW output solved, GeneratorMWSolve | Magnitude of generator MW output. Solved value | MW |  | Calculated by power flow or state estimation solution. This attribute may be used instead of GeneratorAnalogSetNo for solution values. | Real |
| Generator Mvar Output solved, GeneratorMvarSolve | Magnitude of generator MW output. Solved value | Mvar |  | Calculated by power flow or state estimation solution. This attribute may be used instead of GeneratorAnalogSet for solution values. | Real |

Generators (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Generator Analog Values GeneratorAnalogSetNo | Identifies generator’s analog information in Analog data via AnalogSet entry | MW |  |  | integer |
| Dispatch Group Identifier GeneratorDispatchGroupSet | Number of group (GroupSet) to which this unit is assigned to indicate that a single dispatch requirement is determined for the group as if all machines assigned to the group are dispatched as a single unit |  | defaults to unity |  | real |
| Rated Power Factor GeneratorRatedPowerFactor | nameplate power factor |  |  |  | real |
| Type Code or Codes GeneratorMachineType | four-character code describing machine type 1st Character Type G Generator M Motor C Condenser P Pump/Generator O Other 2nd Character S Synchronous I Induction O Other 3rd and 4th Characters 2P 2-pole machine 4P 4-pole machine SD Salient pole with damping SN Salient pole - no damping HC Hydrogen cooled condenser AC Air cooled condenser CR Cylindrical rotor SR Squirrel cage rotor WR Wound rotor OT Other |  | as defined under definition |  | Text |
| Commissioning Date GeneratorCommission | Date the device goes into service | MM/DD/YY |  |  | Date |
| Decommissioning Date GeneratorDecommission | Date the device goes out of service | MM/DD/YY |  |  | Date |
| Generator Type GeneratorType | Identifier of generator type (Coal, Oil, Nuclear, Combined Cycle, etc.) |  | Default = blank |  | Text |
| Generator Ownership Set GeneratorOwnershipSet | Ownership set number (OwnershipSet) from Ownership data (set = 0 implies 100% ownership by control area of terminal bus) |  | Default = 0 |  | Integer |
| Generator Description GeneratorDescription | Text describing this unit |  | Default is blank |  | Text |

Generators (Continued)

| Name | Description |  | Units |  | Defaults |  | Constraints |  | Data Type |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Control Mode GeneratorControlMode | control model to be used PQ = hold Q constant at schedule real power output (PQ mode) PV = adjust Q to hold voltage Loband or voltage Hiband at controlled bus respecting machine control parameters (PV mode) NL = adjust Q to hold voltage loband or voltage high band at controlled bus with no limits applied (PV mode) SW = case swing generator (adjust P and Q) |  |  |  |  |  |  |  | integer |  |
| Controlled Bus Identifier GeneratorControlledBusNo | Number of bus (BusNumber) whose voltage is controlled by this machine |  |  |  |  |  |  |  | integer |  |
| Generator Voltage Regulation Conditions GeneratorVoltageRegulationConditions | Generator Voltage control is activated: NO = not at all PR = pre-contingency only PP = Pre- and post- contingency PO = post-contingency only |  |  |  |  |  |  |  |  |  |
| Minimum Reactive Power Output GeneratorMinQOutput | lower limit for reactive power |  | Mvar |  | defaults to zero |  | less than Maximum Reactive Power Output |  | real |  |
| Maximum Reactive Power Output GeneratorMaxQOutput | upper limit for reactive power |  | Mvar |  | defaults to zero |  | greater than minimum reactive power output |  | real |  |
| Minimum Machine Operating Voltage GeneratorMinOperatingVolt | machine minimum operating voltage |  | per unit on machine base voltage |  | defaults to 0.5 |  |  |  | real |  |
| Maximum Machine Operating Voltage GeneratorMaxOperatingVolt | machine maximum operating voltage |  | per unit on machine base voltage |  | defaults to 1.5 |  |  |  | real |  |
| Generator MW solved, GeneratorMWSolve |  | Magnitude of generator output MW. Solved value |  | MW |  |  |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of GeneratorAnalogSetNo for solution values. Positive into Bus |  | Real |

Generators (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Generator Mvar solved, GeneratorMvarSolve | Magnitude of generator output Mvar. Solved value | Mvar |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of GeneratorAnalogSetNo for solution values. Positive into Bus. | Real |
| Real Power Participation Factor GeneratorMWPartFactor | number representing the relative participation in this machine in adjustment of total real power flowing to this bus from all machines connected to it |  | defaults to unity |  | real |
| Reactive Power Participation Factor GeneratorMvarPartFactor | number representing the relative participation of this machine in adjustment of reactive power with respect to that of all other machines controlling voltage at the same bus |  | defaults to unity |  | real |
| Generator Post-Contingency Response Factor GeneratorPostContRespFact | Percentage of generator MW response to system post-contingency MW imbalance. Assume value will be normalized for each island, and does not need to add to 100. |  |  |  | real |
| Low Control Power Limit MW GeneratorLowControlMW | minimum real power at which machine should be operated | MW |  | mandatory | real |
| Low Economic Power Limit MW GeneratorLowEconMW | minimum real power to which machine should be scheduled | MW |  | mandatory | real |
| High Economic Power Limit MW GeneratorHighEconMW | maximum real power to which machine should be scheduled | MW |  | mandatory | real |
| High Control Power Limit MW GeneratorHighControlMW | maximum real power at which machine should be operated | MW |  | mandatory | real |
| Commitment Priority Rank GeneratorCommitmentPriority | commitment priority. 1 = highest (i.e. must run) |  | defaults to unity |  | integer |

Generators (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Startup Cost GeneratorStartupCost | cost per start | thousands of dollars | defaults to zero |  | real |
| Effective Availability Factor GeneratorEffectiveAvailFactor | factor defining effective availability of the machine | dimensionless probability | defaults to unity |  | real |
| Operating and Maintenance Cost GeneratorOMCost | monthly O & M cost | thousands of dollars per month | defaults to zero |  | real |
| Real Power Dispatch Factor GeneratorMWDispatchFact | factor representing the relative participation of the machines contribution in the total output of the dispatch group to which it is assigned |  | defaults to unity |  | real |
| Fuel Cost GeneratorFuelCost | fuel cost | $ per million Btu |  | mandatory | real |
| Scheduled Charging Power GeneratorSchedChargingMW | scheduled real power flow from machine to bus when charging; same sign convention as real power output for energy storage data | MW |  | mandatory; < 0 | real |
| Scheduled Charging Reactive Power GeneratorSchedChargingMvar | scheduled reactive power flow from machine to bus when charging; same sign convention as reactive power output | Mvar |  | mandatory | real |
| Minimum Charging Power GeneratorMinChargingMW | magnitude of smallest real power output at which machine can be operated when charging | MW |  | mandatory | real |
| Maximum Charging Power GeneratorMaxChargingMW | magnitude of largest real power output at which machine can be operated when charging | MW |  | mandatory | real |
| Transient Reactance GeneratorTransientX | machine transient reactance | per unit on GeneratorBaseMVA and voltage base) |  | mandatory | real |
| Subtransient Reactance GeneratorSubtransientX | machine subtransient reactance | per unit on GeneratorBaseMVA and voltage base |  | mandatory; <Transient Reactance | real |
| Negative Sequence Reactance GeneratorNegSeqX | machine negative sequence reactance | per unit on GeneratorBaseMVA and voltage base |  | mandatory | real |

Generators (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Zero Sequence Reactance GeneratorZeroSeqX | machine zero sequence reactance | per unit on GeneratorBaseMVA and voltage base |  | mandatory | real |
| Armature Resistance GeneratorArmatureR | machine armature resistance | per unit on GeneratorBaseMVA and voltage base |  | mandatory | real |
| Grounding Resistance- 3Rg GeneratorGrounding3Rg | zero sequence resistance of machine grounding device | per unit on GeneratorBaseMVA and voltage base | defaults to zero |  | real |
| Grounding Reactance -3Xg GeneratorGrounding3Xg | zero sequence reactance of machine grounding device | per unit on GeneratorBaseMVA and voltage base | defaults to zero |  | real |

Generator Capability Curve Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Generator Identifier GeneratorNumber | number of generator |  |  | mandatory | integer |
| Real Power GeneratorCapabilityCurveMW | machine real power output at rated conditions | MW |  | mandatory; | real |
| Lower Reactive Power GeneratorCapabilityLowMvar | lower machine reactive power output corresponding to immediately preceding value of real power output | Mvar |  | mandatory; | real |
| Upper Reactive Power GeneratorCapabilityHighMvar | upper machine reactive power output corresponding to immediately preceding value of real power output | Mvar |  | mandatory | real |

Generator Groupings  Data

| Name | Description | Units | Defaults | Constraint | Data Type |
| --- | --- | --- | --- | --- | --- |
| Generator Identifier GeneratorNumber | number of generator |  |  | mandatory | integer |
| Group Identifier GeneratorGroup | number of group (GroupSet) to which assignment is made |  |  | mandatory; | integer |
| Per Unit Assignment to Group GeneratorAssignmentPU | per unit assignment to group | per unit | defaults to unity |  | real |

Generator Heat Rate Curve Data

| Name | Description | Units | Defaults | Constraint | Data Type |
| --- | --- | --- | --- | --- | --- |
| Generator Identifier GeneratorNumber | number of generator |  |  | mandatory | integer |
| Power Output GeneratorHRMW | real power output | MW |  | mandatory; | real |
| Heat Input Rate GeneratorHRMBtu | total heat input rate corresponding to power output value | million Btu per hour |  | mandatory | real |

Generator Output Allocation Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Generator Identifier GeneratorNumber | number of generator |  |  | mandatory | integer |
| Group Identifier GeneratorOutputAllocationGrp | identifier of group (GroupSet) to which following allocation of output is made |  |  | mandatory | integer |
| Allocation Type GeneratorOutputAllocationType | defines method of allocating the output of this machine to the group specified CP = all real power output at allocation value (and the same constant amount when the output is greater) allocated to group CQ = all reactive power output at allocation value (and the same constant amount when the output is greater) allocated to group FP = allocation value is fraction of remaining actual real power output allocated to group after all CP allocations are made FQ = allocation value is fraction of remaining actual reactive power output allocated to group after all CQ allocations are made |  |  | mandatory | Text |
| Allocation Value GeneratorOutputAllocationValue | Allocation Value |  |  |  | real |

Generator  Rating Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Generator Identifier GeneratorNumber | number of generator bus to which machine is connected |  |  | mandatory | integer |
| Rating Identifier GeneratorRatingNumber | rating number RatingNumber |  |  | mandatory; | integer |
| Rating Value GeneratorRatingValue | value of rating for this machine |  |  | mandatory | real |

Groups

| Name | Definition | Units | Default | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Group Set Name GroupSetName | alphanumeric name of group (i.e., proper name - Company XYZ, etc.) |  |  | mandatory; must be unique | Text |
| Group Set Identifier GroupSet | Set number of group |  |  | mandatory; must be unique | integer |
| SubGroups Contained in Set (1,...,N) GroupSetSubgroups | Numbers representing other groups which make up the subgroups of this set (i.e., set numbers of District EAST, District WEST, and District CENTRAL). For lowest level (i.e., no subgroups - Station 123) this is 0 |  |  | Nonzero for groups consisting of subgroups | integer |
| Descriptive Text GroupSetDescription | text describing this group (i.e., Company, Area, District, Loss Zone, etc.) |  |  |  | Text |
| Low level object GroupSetLowLevelObj | If GroupSetSubgroups = 0, then enter object name of low level object (Bus, Line, Generator, Xformer, Shunt, Load, Station,Company, etc.) from basic objects of dictionary |  |  | Should be null if GroupSetSubgroups is non-zero. | Text |
| Low Level Object Number GroupSetLowLevelObjNumber | Number (BusNumber, LineNumber, GeneratorNumber, XformerNumber, ShuntNumber, LoadNumber, StationNumber, CompanyNumber, etc) of low level object type identified in GroupSetLowLevelObj |  |  | Should be null if GroupSetSubgroups is non-zero. | Integer |

Interchange Control

| Name | Definition | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Interchange Group Set Identifier InterchGroupSetNumber | Set number of group (GroupSet) subject to net interchange control |  |  | mandatory | integer |
| Control Flag InterchGroupControlMode | specifies whether generation in group is to be adjusted to control net interchange OFF = off control ON = on control, PR = Pre-contingency only PP = On control, Pre- and Post-contingency PO = Post-contingency only |  | defaults to On |  | integer |
| Scheduled Net Real Power Interchange InterchGroupSchedNetMW | scheduled real power flow across boundary of group; positive for export negative for import | MW |  | mandatory if Transactions not defined, otherwise optional and must total to net of Transactions for InterchangeGroupSetNumber | real |
| Interchange Control Tolerance InterchGroupControlTol | tolerance above and below schedule within which net interchange may lie | MW |  | mandatory | real |
| Actual Net Real Power Interchange InterchGroupActNetMW | actual value of net real power interchange for this group; positive for export negative for import | MW |  |  | real |
| Actual Net Reactive Power Interchange InterchGroupActNetMvar | actual value of net reactive power interchange for this group; positive for export of inductive reactive power | Mvar |  |  | real |
| Controlling Machine Identifier InterchGroupControlGenNumber | identifier of controlling machine, GeneratorNumber |  |  | mandatory unless controlling group is present | Text |
| Descriptive Text InterchGroupDescription | text describing this interchange control area |  |  |  | Text |

Interchange Control (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Group Identifier InterchGroupGenControlGrp | Number (GroupSet) of group whose machines participate in control |  |  | mandatory must exist if controlling machine does not | integer |
| Control Status InterchGroupGenControlGrpMode | control status of this group; OFF = off control ON = on control |  | defaults to zero |  | integer |
| Control Priority InterchGroupGenControlGrpPrior | priority of this group in controlling net interchange; 1 = highest |  | defaults to unity |  | integer |
| Control Participation Factor InterchGroupGenControlPartFact | per unit participation of this group in controlling net interchange of this interchange control area |  | defaults to unity |  | real |

Lines

| Name | Definitions | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Line Number LineNumber | Unique Line representing the line |  |  |  | Integer |
| From Bus Identifier LineFromBusNo | Number of "from" bus of this line (BusNumber) |  |  | Mandatory; if From Bus Name (LineFromBusName) is omitted | Integer |
| From Bus Name LineFromBusName | Name of “from” bus of this line (BusName) |  |  | Mandatory if From Bus Indentifier (LineFromBusNo) is omitted | Text |
| From Bus Section Number LineFromNodeNo | Number of “from” Connectivity node (Connectivity NodeNumber) connection of this line branch |  |  | Required if ModelConnectivityType not equal BM | Integer |
| To Bus Identifier LineToBusNo | Number of "to" bus of this line |  |  | Mandatory; If To Bus Name (LineToBusName) is omitted | Integer |
| To Bus Name LineToBusName | Name of “to” bus of this line |  |  | Mandatory if To Bus Indentifier (LineToBusNo) is omitted |  |
| To Bus Section Number LineToNodeNo | Number of “to” Connectivity node (Connectivity NodeNumber) connection of this line branch |  |  | Required if ModelConnectivityType not equal BM | Integer |
| Circuit Identifier LineCircuit | Alphanumeric circuit identifier to distinguish among several lines joining the same pair of buses |  |  | Mandatory | Text |
| Section Identifier LineSectionId | Number indicating position of this line section in the line |  | Defaults to zero | Sections must be numbered in ascending order beginning with section adjacent to "from" bus; Connectivity Node number. | Integer |
| Commissioning Date LineCommission | Date the device goes into service | MM/DD/YY |  |  | Date |
| Decommissioning Date LineDecommission | Date the device goes out of service | MM/DD/YY |  |  | Date |
| Line Analog Values Set LineAnalogSetNo | Identifies the set of the line’s analog information in analog measurement data via AnalogSet |  |  |  | Integer |
| Line Status LineStatus | Identifies line’s status information in Status measurement data via StatusNumber entry |  |  | Primary use if ModelConnectivityType = BM model is used (i.e., bus model with no topology processing) | Integer |

Lines (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Section Base kV LineSectionBasekV | Base voltage used in calculating section impedances line-to-line RMS if a.c.; Line-to-ground if d.c. | kV | Defaults to base voltage -Base kV of from bus |  | Real |
| Section Series Resistance, R LineSectionR | Series resistance of this section | per unit on system base MVA and section base voltage |  | Mandatory | Real |
| Section Series Reactance, X LineSectionX | Series reactance of this section | per unit on system base MVA and section base voltage |  | Mandatory; for a d.c. line base frequency must be system frequency | Real |
| Shunt Conductance +G LineShuntConductance | Total uniformly distributed shunt conductance of this section | per unit on system base MVA and section base voltage | Defaults to zero |  | Real |
| Shunt Susceptance, +B LineShuntSusceptance | Total uniformly distributed shunt susceptance of this section | per unit on system base MVA and section base voltage |  | Mandatory; for a d.c. line base frequency must be system frequency | Real |
| Line From MW Flow solved, LineFromMWSolve | Magnitude of Line MW flow at From end. Solved value | Mw |  | Calculated by power flow or state estimation solution. This attribute may be used instead of LineAnalogSetNofor solution values. Positive out of bus. | Real |
| Line From Mvar Flow solved, LineFromMvarSolve | Magnitude of Line Mvar flow at From end. Solved value | Mvar |  | Calculated by power flow or state estimation solution. This attribute may be used instead of LineAnalogSetNo for solution values. Positive out of bus. | Real |
| Line To MW Flow solved, LineToMWSolve | Magnitude of Line MW flow at To end. Solved value | MW |  | Calculated by power flow or state estimation solution. This attribute may be used instead of LineAnalogSetNo for solution values. Positive out of bus. | Real |
| Line To Mvar Flow solved, LineToMvarSolve | Magnitude of Line Mvar flow at To end. Solved value | Mvar |  | Calculated by power flow or state estimation solution. This attribute may be used instead of LineAnalogSetNo for solution values. Positive out of bus. | Real |

Lines (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Line Ownership LineOwnershipSet | Owner of this section of line (OwnershipSet number if not 100%, set = 0) |  | Default = 0 | Active attribute if 100 % ownership can be assumed, otherwise ownership set number | Integer |
| Line Name LineName | Alphanumeric line name |  | Defaults to blank |  | Text |
| Type Identifier LineTypeId | Alphanumeric identification of equipment type (e.g. LINE CAPACITOR, TIE, etc.) |  | Defaults to blanks | Optional | Text |
| Line Length LineLength | Length of section | kilometers |  |  | Real |
| Descriptive Text LineDescription | Text describing this section (e.g. shares right of way, etc.) |  |  |  | Text |
| Line From MW solved, LineFromMWSolve | Magnitude of line flow MW at From bus. Solved value | MW |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of LineAnalogSetNo for solution values. | Real |
| Line From Mvar solved, LineFromMvarSolve | Magnitude of line flow Mvar at from bus. Solved value | Mvar |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of LineAnalogSetNo for solution values. | Real |
| Line To MW solved, LineToMWSolve | Magnitude of line flow MW at To Bus. Solved value | MW |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of LineAnalogSetNo for solution values. | Real |
| Line To Mvar solved, LineToMvarSolve | Magnitude of line flow Mvar at To Bus. Solved value | Mvar |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of LineAnalogSetNo for solution values. | Real |
| From Bus Conductance LineFromLumpedCond | Conductance of lumped shunt element connected at "from" bus end of section | per unit on system base MVA and section base voltage | Defaults to zero |  | Real |

Lines (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| From Bus Susceptance LineFromLumpedSuscept | Susceptance of lumped shunt element connected at "from" bus end of section | per unit on system base MVA and section base voltage |  | Mandatory; for a d.c. line base frequency must be system frequency | Real |
| To Bus Conductance LineToLumpedCond | Conductance of lumped shunt element connected at "to" bus end of section | per unit on system base MVA and section base voltage | Defaults to zero |  | Real |
| To Bus Susceptance LineToLumpedSucept | Susceptance of lumped shunt element connected at "to" bus end of section | per unit on system base MVA and section base voltage |  | Mandatory; for a d.c. line base frequency must be system frequency | Real |
| Control Mode LineBypassControlMode | Basis for bypassing this section; NC = no control GO = output of generator LF = flow on line TF = flow on transformer winding |  | Defaults to NC |  | Text |
| Control Priority LineBypassPriority | The priority for sequential bypass control in a line; 1 = highest |  | Defaults to unity |  | Integer |
| Controlled Element LineBypassMonitoredElementNumber | Number of element from LineNumber, GeneratorNumber, or XformerNumber (based on LineBypassControlMode device identified) which is monitored |  |  | Mandatory if LineBypassControlMode is not NC. | Integer |
| Lower MW Flow for Bypass Control LineLowerMWControlFlow | The lower limit of MW band for bypass control of this section; measured as output of generator as flow from controlled bus 1 of branch or as flow into the winding identified for transformer | MW |  | Mandatory | Real |
| Upper MW Flow for Bypass Control LineUpperMWControlFlow | The upper limit of MW band for bypass control of this section; measured as output of generator as flow from controlled bus 1 of branch or as flow into the winding identified for the transformer | MW |  | Mandatory | Real |

Lines (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Bypass Control Action LineBypassAction | Defines bypass control action: CLOP =bypass device closed if monitored flow is inside band defined by Lower MW flow and Upper MW flow and opened if outside band. OPCL = bypass device opened if monitored flow is inside band defined by Lower MW flow and Upper MW flow and closed if outside band. |  |  | Mandatory | Integer |
| Section Zero Sequence Series Resistance LineSelfZeroSeqR | Self zero sequence resistance of this section | per unit on system base MVA and section base voltage |  | Mandatory | Real |
| Section Zero Sequence Series Reactance LineSelfZeroSeqX | Self zero sequence reactance of this section | per unit on system base MVA and section base voltage |  | Mandatory | Real |
| Section Zero Sequence Shunt Conductance LineZeroSeqConductance | Total uniformly distributed shunt zero sequence conductance of this section | per unit on system base MVA and section base voltage | Defaults to zero |  | Real |
| Section Zero Sequence Shunt Susceptance LineZeroSeqSusceptance | Total uniformly distributed shunt zero sequence susceptance of this section | per unit on system base MVA and section base voltage | Defaults to zero |  | Real |
| From Bus Zero Sequence conductance LineFromZeroConductance | Zero sequence conductance of lumped shunt element connected at "from" bus end of section | per unit on system base MVA and section base voltage | Defaults to zero |  | Real |
| From Bus Zero Sequence Susceptance LineFromZeroSusceptance | Zero sequence susceptance of lumped shunt element connected at "from" bus end of section | per unit on system base MVA and section base voltage | Defaults to zero |  | Real |

Lines (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| To Bus Zero Sequence Conductance LineToZeroConductance | Zero sequence conductance of lumped shunt element connected at "to" bus end of section | per unit on system base MVA and section base voltage | Defaults to zero |  | Real |
| To bus Zero Sequence Susceptance LineToZeroSusceptance | Zero sequence susceptance of lumped shunt element connected at "to" bus end of section | per unit on system base MVA and section base voltage | Defaults to zero |  | Real |
| From Bus Grounding Resistance, 3Rg LineFromBus3Rg | Zero sequence resistance of device grounding lumped shunt elements at "from" bus end of section | per unit on same bases as lumped shunt element | Defaults to zero |  | Real |
| From Bus Grounding Reactance, 3Xg LineFromBus3Xg | Zero sequence reactance of device grounding lumped shunt elements at "from" bus end of section | per unit on same bases as lumped shunt element | Defaults to zero |  | Real |
| To Bus Grounding Resistance ,3Rg LineToBus3Rg | Zero sequence resistance of device grounding lumped shunt elements at "to" bus end of section | per unit on same bases as lumped shunt element | Defaults to zero |  | Real |
| To Bus Grounding Reactance, 3Xg LineToBus3Xg | Zero sequence reactance of device grounding lumped shunt element at "to" bus end of section | per unit on same bases as lumped shunt element | Defaults to zero |  | Real |
| Line Group Identifier(1..N) LineGroup | Number of a group (GroupSet) to which this line section is assigned |  |  | Mandatory | Integer |
| Per Unit Assignment to Group(1..N) LineGroupPUAssign | Per unit assignment of this section to this group | per unit | Defaults to unity |  | Real |
| Per Unit Losses Assigned to Group(1..N) LineGroupPULoss | per unit of losses of this line section assigned to this group | per unit | Defaults to unity |  | Real |
| Rating Identifier (1..N) LineRateId | Rating Number for this Rating (RatingNumber) |  |  | Mandatory | Integer |
| Rating Value (1..N) LineRateValue | Rating value for the rating of this branch | As definded by rating units |  | Mandatory, if LineRateId not = 0 or blank | Real |

Line D.C. Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Line data number DCLineNumber | Number of line (LineNumber) with corresponding information for this DC info |  |  | Required | Integer |
| A.C. Bus Identifier DCLineACBusNumber | number of converter a.c. terminal bus (BusNumber) |  |  | mandatory | Integer |
| Converter D.C. Positive Bus Identifier DCLineConverterPosBusNo | number of converter d.c. positive bus zero if ground (BusNumber) |  |  | mandatory or zero | Integer |
| Converter D.C. Negative Bus Identifier DCLineConverterNegBusNo | number of converter d.c. negative bus zero if ground (BusNumber) |  |  | Mandatory or zero | Integer |
| Converter Identifier DCLineConverterName | alphanumeric name of this converter |  |  | mandatory; must be unique among all converters | Text |
| AC Real Power DCLineMwAC | Actual real power flowing from a c bus to the converter positive for rectifier negative for inverter | MW |  | Mandatory | Real |
| A.C. Reactive Power DCLineMvarAC | actual reactive power flowing from a c bus to converter inductive flow to converter is positive | Mvar |  | Mandatory | Real |
| D.C. Voltage DCLineVoltageDC | actual d.c. voltage between converter positive and negative buses | kV |  | Mandatory | Real |
| D.C. Current DCLineCurrentDC | actual d.c. current flowing within the converter the current is positive when flowing from positiive bus to negative bus | amps |  | Mandatory | Real |
| Firing Angle DCLineFiringAngle | actual delay angle (alpha) if a rectifier actual advance angle (gamma) if an inverter | degrees |  | Mandatory 0<value<90 | Real |

Line D.C. Data (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Operating State DCLineOperatingState | actual operating state of converter zero indicates that state is to be inferred from AC Real Power AC Reactive Power DC Voltage DC Current Firing Angle and Nominal Minimum Firing Angle |  | Defaults to 0 | any non zero | Integer |
| Nominal Minimum Firing Angle DCLineNominalMinFiringAng | nominal minimum alpha or gamma angle | degrees |  | mandatory 0 < value < 90 | real |
| Commutating Resistance DCLineCommutaingResistance | effective commutating resistance zero if value is to be determined by application program | ohms |  | Mandatory | Real |
| Commutating Reactance DCLineCommutatingReactance | effective commutating reactance zero if value is to be determined by application program | ohms at a.c. bus base frequency |  | Mandatory | Real |
| Converter Voltage Drop DCLineConverterVoltDrop | forward d.c. voltage drop of this converter | kV | Defaults to zero |  | Real |
| Number of Bridges DCLineNoBridges | Number of equivalent six pulse bridges connected in series in this converter |  |  | Mandatory | Integer |
| D.C. Facility Name DCLineFacilityName | alphanumeric name of dc facility incorporating this converter |  | Defaults to blanks |  | Text |

Line D.C. Data (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Converter Group Identifier (1...n) DCLineConverterGroupId | number of a group to which this converter is assigned |  |  | Mandatory | Integer |
| Per Unit Assignment to Group (1...n) DCLineGroupPUAssign | per unit assignment of this converter to this group | per unit | Defaults to unity |  | Real |
| Per Unit Losses Assigned to Group (1...n) DCLineGroupPULossAssign | per unit of losses of this converter assigned to this group | per unit | defaults to unity |  | Real |
| Descriptive Text DCLineConverterDescription | text describing this converter (e.g. models bipole 12 pulse converter) |  |  |  | Text |
| Rating Identifier (1...n) DCLineRatingId | rating number for this rating (RatingNumber) |  |  | Mandatory | Integer |
| Rating Value (1...n) DCLineRatingValue | rating value for this rating and this converter | as defined by rating |  | Mandatory | Real |
| State Number DCLineOperatingStateNumber | Operating state number |  |  | Mandatory | Integer |
| State Descriptive Text DCLineStateDescription | text describing this converter state |  |  |  | Text |
| Control Objective Code DCLineControlObjCode | type of control objective AMP = current (amps if dc per unit if ac) VMAG = voltage magnitude (kV if dc per unit if ac) VANG = voltage angle (degrees) MW = real power (MW) MVAR = reactive power (MVAR) MVA = total power (MVA) FIRE = firing angle (degrees) FREQ = frequency (hertz) |  |  | Mandatory | Integer |
| Control Priority DCLineControlPriority | priority of this control objective relative to others specified for this operating state 1 = highest |  | Defaults to unity |  | Integer |

Line D.C. Data (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Control Mode DCLineControlMode | type of control mode NONE= no control SETPT = control to setpoint BAND = control to band |  |  | Mandatory | Integer |
| Control Setpoint DCLineControlSetPoint | setpoint value of controlled quantity | as indicated for control objective code |  | Mandatory is control mode is SETPT | Real |
| Control Band Lower Limit DCLineControlBandLowLim | control band lower limit | as indicated for control objective code |  | mandatory if control mode is BAND Control band lower Limit < Control Band Upper Limit | Real |
| Control Band Upper Limit DCLineControlBandHighLim | control band upper limit | as indicated for control objective code |  | mandatory if control mode is BAND Control band lower Limit < Control Band Upper Limit | Real |
| Minimum Firing Angle DCLineControlMinFireAng | minimum firing angle applicable to this control action | degrees |  | mandatory (Minimum Firing Angle < Nominal Firing Angle < Maximum Firing Angle | Real |
| Maximum Firing Angle DCLineControlMaxFireAng | maximum firing angle applicable to this control action | degrees |  | mandatory (Minimum Firing Angle < Nominal Firing Angle < Maximum Firing Angle | Real |

Line D.C. Data (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Monitored Element Type Code DCLineMonitorElementType | Type of element controlled by this converter BUS = bus LINE = Line XFORMER = transformer winding GEN = generator or rotating machine SHUNT = nonsynchronous shunt reactive device ACCONV = converter (a.c. side) DCCONV = converter (d.c. side) |  |  | Mandatory | Integer |
| Monitored Element Identifier DCLineMonitorElementNo | Number of the element from DCLineMonitorElementType which the quantity is monitored for the control objective code |  |  | Mandatory is Monitored element type code is not 1 | Text |
| Controlling Element Type DCLineControlElementType | type of element controlling this converter CONV = converter XFORMER = transformer winding GEN = generator or rotating machine SHUNT = nonsynchronous shunt reactive device |  |  | Mandatory | Integer |
| Controlling Element Identifier DCLineControlElementNo | Number of the element from DCLineControlElementType that is manipulated to control the monitored element to achieve the control objective code |  |  | Mandatory | Text |
| Compounding Resistance DCLineControlCompoundingR | D.C. compounding resistance used in this control action | ohms | defaults to zero |  | Real |

Line Mutual Coupling Data

| Name | Definitions | Units | Default | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| First Line MutualLineA | First line section (LineNumber) associated with mutual coupling data |  |  | mandatory | integer |
| First Line MutualLineB | Second line section (LineNumber) associated with mutual coupling data |  |  | mandatory | integer |
| Zero Sequence Mutual Coupling Resistance MutualZeroSeqR | zero sequence mutual coupling resistance between the first and second line sections identified | per unit on system base MVA and base voltages of coupled branch sections |  | mandatory; the polarity of the mutual coupling is determined by the ordering of the bus numbers from bus to bus for the branch and from bus coupled to bus coupled The "dot" convention applies with the "from" buses specifying the two "dot" ends of the coupled branches. | real |
| Zero Sequence Mutual Coupling Reactance MutualZeroSeqX | zero sequence mutual coupling reactance between first and second line sections identified | per unit on system base MVA and base voltages of coupled branch sections |  | mandatory; the polarity of the mutual coupling is determined by the ordering of the bus numbers from bus to bus for the branch and from bus coupled to bus coupled. The "dot" convention applies with the "from" buses specifying the two "dot" ends of the coupled branches. | real |
| Zero Sequence Mutual Coupling Conductance MutualZeroSeqG | zero sequence mutual total uniformly distributed shunt conductance between this branch section and the branch section declared | per unit on system base MVA and base voltages of the coupled branch sections | defaults to zero |  | real |
| Zero Sequence Mutual Coupling Susceptance MutualZeroSeqB | zero sequence mutual total uniformly distributed shunt susceptance between this branch section and the branch section declared | per unit on system base MVA and base voltages of the coupled branch sections | defaults to zero |  | real |

Load Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Load Number LoadNumber | Unique Number representing load |  |  |  | integer |
| Load Name LoadName | Unique Name for load |  |  |  | text |
| Bus Identifier LoadBusNo | number of bus to which load is connected |  |  | mandatory | integer |
| Bus Section Identifier LoadConnectivityNode | Indicates connectivity node connection point of generator (ConnectivityNodeNumber) |  |  | used when ModelConnectivityType not equal BM | integer |
| Load Identifier LoadID | Alphanumeric identifier to distinguish among multiple loads connected at this bus |  |  | Mandatory | Text |
| Load Status LoadStatus | Identifies load’s status information in Status data via StatusNumber |  | defaults to unity | Primary use if ModelConnectivityType = BM model is used (i.e., bus model with no topology processing) | Integer |
| Load Analog Values LoadAnalogSetNo | Identifies load’s analog information in Analog data via AnalogSet entry |  |  |  | integer |
| Load Model Type LoadModelType | Indicator of load model to be used; CONST = constant MW and MVAR VFUNC = voltage dependent (function) F&V = frequency and voltage dependent GEN = Generator output dependent VTAB= voltage dependent (tabular) INDMOT = induction motor |  | Defaults to CONST |  | Text |
| Load Model Number LoadModelNumber | Model Number corresponding to model type (LoadModelType) |  |  | Mandatory if LoadModelType not CONST | Integer |
| Load Type Identifier LoadConformingType | Identifier of load type (CONFORMING or NONCONFORMING) |  | Defaults to CONFORMING |  | Text |

Load Data (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Load Ownership Set LoadOwnershipSet | Ownership set (OwnershipSet) number from Ownership data (set = 0 implies 100% ownership by control area of terminal bus) |  | Default = 0 |  | Integer |
| Descriptive Text LoadDescription | Text describing this load (e.g. RESIDENTIAL, COMMERCIAL, etc.) |  |  |  | Text |
| Minimum Voltage LoadModelMinVoltage | Minimum voltage for which this load model is valid | per unit | Defaults to zero | Minimum Voltage < Maximum Voltage | Real |
| Maximum Voltage LoadModelMaxVoltage | Maximum voltage for which this load model is valid | per unit | Defaults to infinity (no maximum) | Minimum Voltage @ Maximum Voltage | Real |
| Alternate Bus Indentifier LoadAltBusNo | Identifier of the bus (BusNumber) to which this load is to be connected if the load flow bus identifier is deengerized |  | Defaults to zero |  | Integer |
| Minimum Real Power LoadMinMW | Minimum real power that can be consumed under any condition | MW | Defaults to minus infinity (no Minimum) | Minimum Real Power < Maximum Real Power | Real |
| Maximum Real Power LoadMaxMW | Maximum real power that can be consumed under any condition | MW | Defaults to infinity (no maximum) | Minimum Real Power < Maximum Real Power | Real |
| Reference Real Power LoadReferenceMW | Load reference real power at one per unit voltage and frequency used for scaling purposes | MW | Defaults to zero (no scaling) | Must be positive | Real |
| Minimum Reactive Power LoadMinMvar | Minimum reactive power consumed for any conditions; inductive load is positive | Mvar | Defaults to minus infinity (no minimum) | Minimum Reactive Power < Maximum Reative Power | Real |
| Maximum Reactive Power LoadMaxMvar | Maximum reactive power consumed for any conditions;inductive load is positive | Mvar | Defaults to infinity (no maximum) | Maximum Reactive Power > Minimum Reactive Power | Real |
| ReferenceReactive Power LoadReferenceMvar | Load reference reactive power at one per unit voltage and frequency used for scaling purposes; inductive load is positive | Mvar | Defaults to zero (no scaling) |  | Real |

Load Data (Continued)

| Name | Description | Units | Defaults | Constraints |  | Data Type |
| --- | --- | --- | --- | --- | --- | --- |
| Group Identifier (1...n) LoadGroupId | Identifier of group (GroupSet) to which this load is assigned |  |  |  | Integer |  |
| Per Unit Assignment to Group (1...n) LoadGroupAssignPU | per unit assignment to group | per unit | defaults to unity |  |  |  |
| Commissioning Date LoadCommissioningDate | Date the device goes into service | MM/DD/YY |  |  |  | Date |
| Decommissioning Date LoadDecommissioningDate | Date the device goes out of service | MM/DD/YY |  |  |  | Date |
| Load Negative Sequence Conductance LoadNegSeqConductance | negative sequence conductance of the load | per unit on the system MVA base and bus base voltage |  | Mandatory |  | Real |
| Load Negative Sequence Susceptance LoadNegSeqSusceptance | negative sequence susceptance of the load | per unit on the system MVA base and bus base voltage |  | Mandatory |  | Real |
| Load Zero Sequence Conductance LoadZeroSeqConductance | zero sequence conductance of the load | per unit on the system MVA base and bus base voltage |  | Mandatory |  | Real |
| Load Zero Sequence Susceptance LoadZeroSeqSusceptance | zero sequence susceptance of the load | per unit on the system MVA base and bus base |  |  |  |  |
| Load Grounding Resistance 3Rg LoadGrounding3Rg | zero sequence resistance of load grounding device | per unit on system MVA base and bus base voltage | Defaults to zero |  |  | Real |
| Load Grounding Reactance 3Xg LoadGrounding3Xg | zero sequence reactance of load grounding device | per unit on system MVA base and bus base voltage | Defaults to Zero |  |  | Real |
| Load MW solved, LoadMwSolve | Magnitude of Load MW. Solved value | MW |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of LoadAnalogSetNo for solution values. Positive out of Bus. |  | Real |
| Load Mvar solved, LoadMvarSolve | Magnitude of Load Mvar. Solved value | Mvar |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of LoadAnalogSetNo for solution values. Positive out of Bus. |  | Real |

Load (Voltage Dependent Model) Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Voltage Dependent Model Number LoadVoltDependModelNo | Unique identifier for this model type corresponding to LoadModelType = VFUNC |  |  | Mandatory,Unique | Integer |
| Voltage Dependent Load Model | Pact = (a + a v + a v@)Po @ @ @ Qact = (a + a v + a v@)Qo @ @ @ a + a + a = 1 @ @ @ a + a + a = 1 @ @ @ |  |  | Where Po = nominal real load Qo = nominal reactive load v = per unit magnitude of voltage vmag at bus to which load is connected Pact = actual real load consumed Qact = actual reactive load consumed | Model |
| Values of Coefficient a (1...6) LoadVoltDependModelCoeffValue | Fraction of load that is constant MVA constant current and constant admittance for real and reactive power as used in the voltage dependent load model | per unit |  | Mandatory | Real |

Load (Voltage and Frequency Dependent Model) Data

| Name | Description | Units | Defaults |  | Constraints |  | Data Type |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Voltage and Freq Dependent Model Number LoadVandFDependModelNo | Unique identifier for this model type corresponding to LoadModelType = V&F |  |  | Mandatory,Unique |  | Integer |  |
| Voltage and Frequency dependent Load Model | Pact = (a @ + a + a)Po @ @ @ Qact = (a + a + a)Qo @ @ @ a + a + a = 1 @ @ @ a + a + a = 1 @ @ @ |  |  |  | Where Po = nominal real load Qo = nominal reactive load v = per unit magnitude of voltage vmag at bus to which load is connected Pact = actual real load consumed Qact = actual reactive load consumed f = per unit frequency at bus to which load is connected |  | Model |
| Values of Coefficient a (1...6) LoadVandFDependCoeffValueA | Coefficients used in voltage and frequency dependent load model | per unit |  |  | Mandatory |  | Real |
| Values of Exponents n (1...6) LoadVandFDependExpValueN | Voltage exponents used in voltage and frequency dependent load model |  |  |  | Mandatory |  | Real |
| Values of Exponents m (1...6) LoadVandFDependExpValueM | Frequency exponents used in voltage and frequency load model |  |  |  | Mandatory |  | Real |

Load (Tabular Definition of Power vs Voltage) Data

| Name | Definition | Units | Defaults |  | Constraints |  | Data Type |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Voltage Tabular Definition Model Number LoadVTabDependModelNo | Unique identifier for this model type corresponding to LoadModelType = VTAB |  |  | Mandatory,Unique |  | Integer |  |
| Tabular Definition of power versus voltage | Data for load tabular definition of real and reactive power versus voltage Pact = (tabular function of v) Po Qact = (tabular function of v)Qo |  |  |  | Where Po = nominal real load Qo = nominal reactive load v = per unit magnitude of voltage vmag at bus to which load is connected Pact = actual real load consumed Qact = actual reactive load consumed |  | Model |
| Values of v (1...n) LoadVTabDependVoltValue | Voltage magnitude values for tabular definition of real and reactive load | per unit |  |  | Mandatory; monotonically increasing set |  | Real |
| Values of (Pact/Po) (1...n) LoadVTabDependMwValue | Value of real power load at voltage | per unit of nominal load real power |  |  | Mandatory |  | Real |
| Values of (Qact/Qo) (1...n) LoadVTabDependMvarValue | Value of reactive power load at voltage | per unit of nominal load reactive power |  |  | Mandatory; inductive load is positive |  | Real |

Load (Induction Motor Model) Data

| Name | Description | Units | Defaults |  | Constraints |  | Data Type |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Voltage Tabular Definition Model Number LoadIndMotModelNo | Unique identifier for this model type corresponding to LoadModelType = INDMOT |  |  | Mandatory,Unique |  | Integer |  |
| Induction Motor Equivalent circuit | Data for load induction motor equivalent circuit parameters |  |  |  |  |  | Model |
| Motor Base MVA LoadIndMotBaseMVA | Motor base MVA | MVA |  |  | Mandatory |  | Real |
| Value of RA LoadIndMotRAValue | Armature resistance | per unit on motor MVA base and base voltage of bus to which this load is connected. |  |  | Mandatory |  | Real |
| Value of LA LoadIndMotLAValue | Armature inductance | per unit on motor MVA base and base voltage of bus |  |  | Mandatory |  | Real |
| Value of LM LoadIndMotLMValue | Mutual inductance | per unit on motor MVA base and base voltage of bus |  |  | Mandatory |  | Real |
| Value of R1 LoadIndMotR1Value | First loop resistance | per unit on motor MVA base and base voltage of bus |  |  | Mandatory |  | Real |
| Value of L1 LoadIndMotL1Value | First loop inductance- per unit on motor MVA base and base voltage of bus |  |  |  | Mandatory |  | Real |
| Value of R2 LoadIndMotR2Value | Second loop resistance per unit on motor MVA base and base voltage of bus |  |  |  | Mandatory |  | Real |
| Value of L2 LoadIndMotL2Value | Second loop inductance | per unit on motor MVA base and base voltage of bus to which this load is connected |  |  | Mandatory |  | Real |

Load (Generator Dependent Model) Data

| Name | Description | Units | Defaults |  | Constraints |  | Data Type |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Generator Dependent Model Number LoadGenDependModelNo | Unique identifier for this model type corresponding to LoadModelType = GEN |  |  | Mandatory,Unique |  | Integer |  |
| Generator Dependent Load | defines this load to be dependent on a specific generator for the load nominal power. The representation has the form |  |  |  | Po = PB + KSCH * PGEN + KMB * MBASE Qo = KQP * Po where PGEN = generator actual power MBASE = the generator MVA base Po = load nominal real power Qo = load nominal reactive power load is in service only when machine status and load status are connected |  | Model |
| Machine Identifier LoadGenDependUnitNumber | Identifier (GeneratorNumber) of machine on which load depends |  |  |  | mandatory |  | Text |
| Value of PB LoadGenDependPBValue | nominal base real power consumed | MW |  |  | mandatory @ 0 |  | Real |
| Value of KQP LoadGenDependKQPValue | ratio of reactive load to real load | Mvar/MW |  |  | Mandatory |  | Real |
| Value of KSCH LoadGenDependKSCHValue | fraction of generator real power output | per unit |  |  | mandatory 0 @ value @ 1.Real |  |  |
| Value of KMB LoadGenDependKMBValue | ratio of load component to generator base MVA | MW/MVA |  |  | Mandatory |  | Real |

Ownership Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Ownership Set Number OwnershipSet | Unique number for ownership set |  |  | Mandatory | Integer |
| Ownership Set Name OwnershipSetName | Name of Ownership set |  |  |  | Text |
| Group Set member number (1,...,N) OwnershipSetMemberNumber | Number of group set (GroupSet) that is an owner in this set (i.e., a group set number representing a Company) |  |  |  | Integer |
| Group Set Member’s Ownership percentage (1,...,N) OwnershipSetMemberPercent | Percentage that member (OwnershipSetMemberNumber)in the ownership set |  |  |  | Real |

Ratings

| Name | Definition | Units | Default | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Rating Name RatingName | alphanumeric rating identifier |  |  | mandatory; must be unique | Text |
| Rating Identifier RatingNumber | Unique number of this rating |  |  | mandatory must be unique | integer |
| Rating Physical Units RatingUnits | alphanumeric identifier of units in which this rating is expressed. The following abbreviations are recommended current- AMPS or KA volt-amperes- MVA or KVA real power- MW or KW reactive power- MVAR or KVAR voltage- KV or V per unit - PU for amps, kv, mw, mvar, mva Other abbreviation may be used when necessary |  |  | mandatory | Text |
| Descriptive Text RatingDescription | description of this rating |  |  |  | Text |

Shunt (Nonsychronous) Devices

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Shunt Number ShuntNumber | Unique Number representing shunt |  |  |  | integer |
| Shunt Name ShuntName | Unique Name for shunt |  |  |  | text |
| Bus Identifier ShuntBusNo | number of bus (BusNumber)to which shunt is connected |  |  | mandatory | integer |
| Bus Section Identifier ShuntConnectivityNode | indicates bus section (ConnectivityNodeNumber) connection point of shunt |  |  | used when ModelConnectivityType not equal BM | integer |
| Circuit Identifier ShuntCircuit | circuit identifier of branch on which device is connected |  |  | mandatory if branch | Integer |
| Commissioning Date ShuntCommission | Date the device goes into service | MM/DD/YY |  |  | Date |
| Decommissioning Date ShuntDecommission | Date the device goes out of service | MM/DD/YY |  |  | Date |
| Device Identifier ShuntUnitNumber | alphanumeric identifier to distinguish among multiple devices connected at a bus or branch |  |  | mandatory; must be unique among all such devices having a common bus whether bus or branch connected | Integer |
| Shunt Status ShuntStatus | Identifies shunt’s status information in Status data via StatusNumber entry |  |  | Primary use if ModelConnectivityType = BM model is used (i.e., bus model with no topology processing) | Integer |
| Device MVA Base ShuntBaseMVA | MVA of this device either system (BaseMVA) or device | MVA |  | mandatory | real |
| Device Base Voltage ShuntBasekV | base voltage of this device | kV |  | mandatory | real |
| Shunt Analog Values ShuntAnalogSetNo | Identifies shunt’s analog information in Analog data via AnalogSet entry |  |  |  | integer |

Shunt (Nonsychronous) Devices (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Shunt Voltage Regulation Conditions ShuntVoltageRegConditions | Shunt Voltage control is activated: NO = not at all PR = pre-contingency only PP = Pre- and post- contingency PO = post-contingency only |  |  |  |  |
| Group Identifier (1...n) ShuntGroup | number of group (GroupSet) to which device is assigned |  |  | Mandatory | Integer |
| Per Unit Assignment to Group (1...n) ShuntAssignmentPU | per unit assignment to group | per unit | defaults to unity |  | Real |
| Per Unit Losses Assigned to Group (1...n) ShuntAssignedLossPU | per unit assigned to losses to group | per unit | defaults to unity |  | Real |
| Descriptive Text ShuntDescription | text describing this device |  |  |  | Text |
| Shunt Ownership Set ShuntOwnershipSet | OwnershipSet number from Ownership data (set = 0 implies 100% ownership by control area of terminal bus) |  | Default = 0 |  | Integer |
| Type Identifier ShuntType | alphanumeric identifier of this device (Capacitor, Reactor, other) |  | defaults to blanks |  | Text |
| Control Mode ShuntControlMode | defines control objective to be used in changing this device NONE = none (fixed susceptances in all blocks) VOLT = hold voltage at designated bus between control limits Lower and Upper MVAR = hold MVAR flow between designated buses within control limits Lower MVAR flow and Upper MVAR flow as measured at "from" bus flowing into branch or transformer |  | defaults to NONE |  | Integer |

Shunt (Nonsychronous) Devices (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Controlled Element Bus ShuntControlBusNo | defines bus at which voltage is to be held within control limits if ShuntControlMode is VOLT or defines bus into which MVAR flow is controlled if control mode is MVAR. |  | bus to which the device is connected |  | Integer |
| Identifier of Controlled Line or Transformer ShuntControlElementNo | Defines line (LineNumber) or transformer (XformerNumber) in which Mvar Flow is controlled when XformerTCUL ControlMode is Mvar |  |  | Mandatory if ShuntControlMode is MVAR or NONE | Integer |
| Controlled Element Type ShuntControlElementType | Element type LINE or XFORMER which Mvar flow is controlled |  |  | Mandatory if ShuntControlMode is MVAR | Text |
| Lower MVAR Flow Limit ShuntLowerMVARLimit | minimum desired MVAR flow if ShuntControlMode is MVAR positive value indicates flow from controlled element bus 1 to controlled element bus 2 or flow into winding | MVAR |  | mandatory if Mandatory if ShuntControlMode is MVAR Lower Mvar flow limit < Upper MVAR flow limit | Real |
| Upper MVAR Flow Limit ShuntUpperMVARLimit | maximum desired Mvar flow if ShuntControlMode is MVAR positive value indicates flow from controlled element bus 1 to controlled element bus 2 or flow into winding MVAR |  |  | mandatory if ShuntControlMode is MVAR Lower Mvar flow limit < Upper Mvar flow limit | Real |
| Max. Regulating voltage Value ShuntMaxRegVoltage | Value at which shunt will change out to lower voltage (i.e. capacitor lower output, reactor increase output) |  |  |  | Real |
| Min. Regulating voltage Value ShuntMinRegVoltage | Value at which shunt will change out to raise voltage (i.e. capacitor increase output, reactor lower output) |  |  |  | Real |

Shunt (Nonsychronous) Devices (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Loss Factor for Inductors ShuntInductorLossFactor | ratio of inductor real power loss to reactive power consumption | MW/Mvar | defaults to zero |  | Real |
| Number of Discrete Susceptance Values Available in Block (1...n) ShuntBlockSusceptValueNo | number of discrete susceptance values available for control action on this block. Zero for continuously variable adjustment |  | defaults to zero | must be nonzero for stepwise control | Integer |
| Block Minimum Susceptance (1...n) ShuntBlockMinSusceptance | minimum susceptance of this block (inductive susceptance is negative) | per unit on bases device base MVA and device base voltage |  | Mandatory block must consist of only capacitors or only inductors | Real |
| Block Maximum Susceptance (1...n) ShuntBlockMaxSusceptance | maximum susceptance of this block (inductance susceptance is negative) | per unit on bases device base MVA and device base voltage |  | Mandatory block must consist of only capacitors or only inductors | Real |
| Block Effective Susceptance (1...n) ShuntBlockSusceptance | susceptance of the part of this block that is utilized (inductive is negative) | per unit on bases device base MVA and device base voltage | defaults to zero | Mandatory block must consist of only capacitors or only inductors | Real |
| Block Connection Type (1...n) Shunt BlockConnectionType | alphanumeric code to identify block connection type GY = grounded y GZ = grounded zig-zag UY = ungrounded y DE = delta |  | defaults to blanks |  | Text |

Shunt (Nonsychronous) Devices (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Shunt MW solved, ShuntMWSolve | Magnitude of Shunt output MW. Solved value | MW |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of ShuntAnalogSetNo for solution values. Positive out of Bus. | Real |
| Shunt Mvar solved, ShuntMvarSolve | Magnitude of Shunt output Mvar. Solved value | Mvar |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of ShuntAnalogSetNo for solution values. Positive out of Bus. | Real |
| Zero Sequence Conductance (1...n) ShuntZeroSeqConductance | zero sequence conductance of block with all steps switched on | per unit on bases device base MVA and device base voltage |  | Mandatory | real |
| Zero Sequence Susceptance (1...n) ShuntZeroSeqSusceptance | zero sequence susceptance of block with all steps switched on | per unit on bases device base MVA and device base voltage |  | mandatory;Real |  |
| Grounding Resistance 3Rg (1...n) ShuntGrounding3Rg | effective zero sequence resistance of grounding device | per unit on bases device base MVA and device base voltage | defaults to zero |  | Real |
| Grounding Reactance 3Xg (1...n) ShuntGrounding3Xg | effective zero sequence reactance of grounding device | per unit on bases device base MVA and device base voltage | defaults to zero |  | Real |

Station Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Station Number StationNumber | Unique number identifying station data |  |  | Mandatory, if this type data is used by Bus (BusStationLocation). Use of Station object is optional if Group Object is used to group Buses (BusLocation) | Integer |
| Station Name StationName | Name of station |  |  | Optional | Text |
| Company location StationCompanyLocation | Location of station within the Company object (CompanyNumber) |  |  | Optional. Use of Group object may be used to group stations into company (or any other grouping such as districts) | Integer |

Status Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Status Number StatusNumber | Unique number identifying status data |  |  | Mandatory, if this type data is used | Integer |
| Status Name StatusName | Name of status |  |  |  | Text |
| Status Code StatusValue | Current status, where: OP = Open, Off,All terminals disconnected CL = Closed, On, All terminals connected OE = Open Ended, at least one terminal closed and at least one open AV = Available (Offline but Available for use as a control) Q = Questionable B = Bypassed by zero impedance with no control BC = Bypassed by zero impedance but with control NB = not bypassed by zero impedance but with control TR = Traveling from one static status to another |  |  |  | Text |
| Normal Status NormalStatus | Normal status, where: status options are the same as for Status (StatusValue) |  |  |  | Text |

Switching Device

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Switching Device Number SwitchNumber | Unique number identifying switching device |  |  | Mandatory, if this type data is used | Integer |
| Switching Device Name SwitchName | Name describing switching device |  |  | Optional | Text |
| “From” Connectivity Node Number SwitchFromNode | Number of “From” Connectivity Node (Connectivity NodeNumber) |  |  |  | Integer |
| “To” Connectivity Node Number SwitchToNode | Number of “To” Connectivity Node (Connectivity NodeNumber) |  |  |  | Integer |
| Commissioning Date SwitchCommission | Date the device goes into service | MM/DD/YY |  |  | Date |
| Decommissioning Date SwitchDecommission | Date the device goes out of service | MM/DD/YY |  |  | Date |
| Switch Device Status Measurement SwitchStatus | Status Measurement Number (StatusNumber) for Switching Device |  |  |  | Integer |
| Switching Device Type SwitchType | Type of Switching Device, where: P = Pseudo or fictitious device CB = Circuit breaker MO = Motor Operated switch M = Manual Switch F = Fuse O = Other |  |  | Optional | Text |
| Switching Device Ownership Set SwitchOwnershipSet | OwnershipSet number from Ownership data (set = 0 implies 100% ownership by control area of terminal bus) |  | Default = 0 |  | Integer |

Transactions

| Name | Definition | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Transaction Number TransactionNumber | Number of transaction |  |  | mandatory; Unique identifier | integer |
| Transaction Name TransactionName | Name of transaction |  | Default = blank |  | text |
| Identifier of From Group TransactionFromGroupNumber | Group set (GroupSet) number of first party (From) in the scheduled interchange transaction |  |  |  | integer |
| Identifier of To Group TransactionToGroupNumber | Group set (GroupSet) number of second party (To) in the scheduled interchange transaction |  |  | mandatory | integer |
| Scheduled Real Power Exchange TransactionSchedMW | scheduled real power exchange from first party exclusive group to second party exclusive group | MW |  | mandatory | real |
| Transaction Description TransactionDescription | Textual description of transaction |  |  |  | text |

Transformer

| Name | Definition | Units | Default | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Transformer Number XformerNumber | Unique Number representing transformer |  |  |  | integer |
| Transformer Name XformerName | Unique Name for transformer |  |  |  | text |
| Commissioning Date XformerCommission | Date the device goes into service | MM/DD/YY |  |  | Date |
| Decommissioning Date XformerDecommission | Date the device goes out of service | MM/DD/YY |  |  | Date |
| Bus Identifier - A,PRIMARY XformerPrimaryBusNo | number of bus (BusNumber) to which winding A is connected |  |  | mandatory | integer |
| Bus Identifier - B,SECONDARY XformerSecondaryBusNo | number of bus (BusNumber) to which winding B is connected |  |  | mandatory | integer |
| Bus Identifier - C,TERIARY XformerTertiaryBusNo | number of bus (BusNumber) to which winding C is connected |  |  | must be zero for 2-winding transformer; mandatory for 3-winding transformer | integer |
| Bus Identifier - D, QUATENARY XformerQuatBusNo | number of bus to which winding D is connected |  |  | must be zero for 2 or 3 winding transformer; mandatory for 4-winding transformer | integer |
| Primary Bus Section Number XformerPriNodeNo | Number of Primary winding Connectivity node (Connectivity NodeNumber) connection of this transformer |  |  | Required if ModelConnectivityType not equal BM | Integer |
| Secondary Bus Section Number XformerSecNodeNo | Number of Secondary winding Connectivity node (Connectivity NodeNumber) connection of this transformer |  |  | Required if ModelConnectivityType not equal BM | Integer |
| Tertiary Bus Section Number XformerTertNodeNo | Number of Tertiary winding Connectivity node (Connectivity NodeNumber) connection of this transformer |  |  | Required if ModelConnectivityType not equal BM | Integer |
| Quatenary Bus Section Number XformerQuatNodeNo | Number of Quatenary winding Connectivity node (Connectivity NodeNumber) connection of this transformer |  |  | Required if ModelConnectivityType not equal BM | Integer |
| Transformer Identifier XformerCircuit | alphanumeric transformer identifier to distinguish uniquely among several transformers connected to the same bus |  |  | mandatory | Text |

Transformers (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Transformer Voltage Regulation Conditions XformerVoltRegCondition | Transformer Voltage control is activated: NO = not at all PR = pre-contingency only PP = Pre- and post- contingency PO = post-contingency only |  |  |  |  |
| Transformer Status XformerStatus | Identifies transformer’s status information in Status data via StatusNumber |  | Defaults to unity | Primary use if ModelConnectivityType = BS or BO model is used (i.e., bus model with no topology processing) | Integer |
| Descriptive Text XformerDescription | text describing this transformer |  |  |  | Text |
| Transformer Base MVA XformerBaseMVA | Base used in calculation of per unit parameters; maybe system (BaseMVA) or device base | MVA | defaults to system MVA base |  | real |
| Transformer Ownership Set XformerOwnershipSet | Ownership set number (OwnershipSet) from Ownership data (set = 0 implies 100% ownership by primary bus owner) |  | Default = 0 |  | Integer |
| Transformer Analog Values XformerAnalogSetNo | Identifies transformer’s analog information in Analog data via AnalogSet entry |  |  | mandatory | integer |
| Transformer From MW solved, XformerFromMwSolve | Magnitude of Transformer flow MW at From bus. Solved value | MW |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of XformerAnalogSetNo for solution values. Positive out of bus. | Real |
| Transformer From Mvar solved, XformerFromMvarSolve | Magnitude of Transformer flow Mvar at from bus. Solved value | Mvar |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of XformerAnalogSetNo for solution values. Positive out of bus. | Real |

Transformers (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Xformer To MW solved, XformerToMwSolve | Magnitude of Xformer flow MW at To Bus. Solved value | MW |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of XformerAnalogSetNo for solution values. Positive out of bus. | Real |
| Transformer To Mvar solved, XformerToMvarSolve | Magnitude of Transformer flow Mvar at To Bus. Solved value | Mvar |  | Optional; Calculated by power flow or state estimation solution. This attribute may be used instead of XformerAnalogSetNo for solution values. Positive out of bus. | Real |
| Resistance - Bus A to Bus B XformerPri-SecR | s.c. - test resistance winding A to winding B | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory | real |
| Reactance - Bus A to Bus B XformerPri-SecX | s.c. - test reactance winding A to winding B | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory | real |
| Resistance - Bus B to Bus C XformerSec-TertR | s.c. - test resistance winding B to winding C | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 3 or 4 winding | real |
| Reactance - Bus B to Bus C XformerSec-TertX | s.c. - test reactance winding B to winding C | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 3 or 4 winding | real |
| Resistance - Bus C to Bus A XformerTert-PriR | s.c. - test resistance winding C to winding A | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 3 or 4 winding | real |
| Reactance - Bus C to Bus A XformerTert-PriX | s.c. - test reactance winding C to winding A | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 3 or 4 winding | real |

Transformers (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Resistance - Bus A to Bus D XformerPri-QuatR | s.c. - test resistance winding A to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 4 winding | real |
| Reactance - Bus A to Bus D XformerPri-QuatX | s.c. - test reactance winding A to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 4 winding | real |
| Resistance - Bus B to Bus D XformerSec-QuatR | s.c. - test resistance winding B to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 4 winding | real |
| Resistance - Bus A to Bus D XformerPri-QuatR | s.c. - test resistance winding A to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 4 winding | real |
| Reactance - Bus A to Bus D XformerPri-QuatX | s.c. - test reactance winding A to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 4 winding | real |
| Resistance - Bus B to Bus D XformerSec-QuatR | s.c. - test resistance winding B to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 4 winding | real |
| Reactance - Bus B to Bus D XformerSec-QuatX | s.c. - test reactance winding B to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 4 winding | real |
| Resistance - Bus C to Bus D XformerTert-QuatR | s.c. - test resistance winding C to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 4 winding | real |
| Reactance - Bus C to Bus D XformerTert-QuatX | s.c. - test reactance winding C to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  | mandatory if 4 winding | real |
| Zero Resistance - Bus A to Bus B XformerPri-SecZeroR | - s.c. zero sequence test resistance winding A to winding B | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  |  | real |
| Zero Reactance - Bus A to Bus B XformerPri-SecZeroX | s.c. zero sequence test reactance winding A to winding B | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  |  | real |

Transformers (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Zero Resistance - Bus B to Bus C XformerSec-TertZeroR | - s.c. zero sequence test resistance winding B to winding C | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  |  | real |
| Zero Reactance - Bus B to Bus C XformerSec-TertZeroX | s.c. zero sequence test reactance winding B to winding C | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  |  | real |
| Zero Resistance - Bus C to Bus A XformerTert-PriZeroR | - s.c. zero sequence test resistance winding C to winding A | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  |  | real |
| Zero Reactance - Bus C to Bus A XformerTert-PriZeroX | s.c. zero sequence test reactance winding C to winding A | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  |  | real |
| Zero Resistance - Bus A to Bus D XformerPri-QuatZeroR | - s.c. zero sequence test resistance winding A to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  |  | real |
| Zero Reactance - Bus A to Bus D XformerPri-QuatZeroX | s.c. zero sequence test reactance winding A to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  |  | real |
| Zero Resistance - Bus B to Bus D XformerSec-QuatZeroR | - s.c. zero sequence test resistance winding B to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  |  | real |
| Zero Reactance - Bus B to Bus D XformerSec-QuatZeroX | s.c. zero sequence test reactance winding B to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  |  | real |
| Zero Resistance - Bus C to Bus D XformerTert-QuatZeroR | - s.c. zero sequence test resistance winding C to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  |  | real |
| Zero Reactance - Bus C to Bus D XformerTert-QuatZeroX | s.c. zero sequence test reactance winding C to winding D | per unit on XformerBaseMVA and base voltage of winding energized in the s.c. test |  |  | real |
| Type Identifier XformerType | alphanumeric identifier of equipment type (e.g. AUTO GSU) |  | defaults to blanks |  | Text |

Transformer Grouping Data

| Name | Definitions | Units | Default | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Transformer Number XformerNumber | Unique Number representing transformer |  |  |  | integer |
| Group Identifier XformerGroup | number of a group (GroupSet) to which this transformer is assigned |  |  | mandatory | integer |
| Per Unit Assignment to Group XformerAssignmentPU | per unit assignment of this transformer to this group | per unit | defaults to unity |  | real |
| Per Unit Losses Assigned to Group XformerAssignedLossPU | per unit of losses of this transformer assigned to this group | per unit | defaults to unity |  | real |

Transformer Winding Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Transformer Number XformerNumber | Unique Number representing transformer |  |  | Matches Transformer from Transformer object data | integer |
| Winding Bus Identifier XformerWindingBusNo | number of Bus (BusNumber) to which this winding is connected |  |  | mandatory, Must match a bus for A,B,C,or D windiing for TransformerNumber | integer |
| Winding Type XformerWindingType | alphanumeric code to identify the winding type GY = grounded Y GA = grounded Y auto-transformer UY = ungrounded Y DE = delta GZ = grounded zig-zag UZ = ungrounded zig-zag SC = Scott connected OD = open delta |  | defaults to blanks | mandatory | Text |
| Voltage Base XformerVoltageBase | voltage base used in expressing transformer winding data | kV |  | mandatory | real |
| Magnetizing Conductance XformerMagnetizingCond | o.c. test conductance of the winding | per unit on XformerBaseMVA and winding base voltage | defaults to zero |  | real |
| Magnetizing Susceptance XformerMagnetizingSusceptance | o.c. test susceptance of the winding | per unit on XformerBaseMVA and winding base voltage | defaults to zero |  | real |
| Zero Magnetizing Conductance XformerMagnetizingCondZero | zero sequence o.c. test conductance of winding | per unit on XformerBaseMVA and base voltage of winding |  |  | real |
| Zero Magnetizing Susceptance XformerMagnetizingSusceptanceZero | zero sequence o.c. test susceptance of winding | per unit on XformerBaseMVA and base voltage of winding |  |  | real |

Transformer Winding Data (Continued)

| Name | Description | Unit | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Grounding Resistance- 3Rg XformerGrounding3Rg | zero sequence resistance of grounding device connected to neutral of winding | per unit on XformerBaseMVA and base voltage of winding | zero if winding is grounded otherwise infinity |  | real |
| Grounding Reactance- 3Xg XformerGrounding3Xg | zero sequence reactance of grounding device connected to neutral of winding | per unit on XformerBaseMVA and base voltageof winding | zero if winding is grounded otherwise infinity |  | real |

Transformer Manually Adjusted Tap Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Transformer Number XformerNumber | Unique Number representing transformer |  |  |  | integer |
| Winding Bus Identifier XformerWindingBusNo | number of Bus (BusNumber) to which this winding is connected |  |  | mandatory, Must match a bus for A,B,C,or D windiing for TransformerNumber | integer |
| Actual Manually Set Tap Voltage XformerActManualTapActVoltage | o.c. voltage in winding at present actual manually set tap position | kV | defaults to winding base voltage | must be a permissible value | real |
| Permissible Manually Set Tap Voltages (1..N) XformerManualTapPermissibleVoltage | the permissible values of o.c. tapped winding voltage | kV | defaults to value of the actual manually set tap voltage | one member of this set must be equal to actual manually set tap voltage monotonically increasing order | real |
| Impedance Adjustment Factor (1..N) XformerManualTapImpedAdjFactor | factor by which total leakage resistance/ reactance/ impedance (A to B)of transformer is multiplied when manually adjusted tap is in this position |  | defaults to unity | valid only for two winding transformer models must be unity if 3 or 4 winding nonzero | real |

Transformer Winding Rating Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Transformer Number XformerNumber | Unique Number representing transformer |  |  |  | integer |
| Winding Bus Identifier XformerWindingBusNo | number of Bus (BusNumber) to which this winding is connected |  |  | mandatory, Must match a bus for A,B,C,or D windiing for TransformerNumber | integer |
| Rating Number XformerWindingRatingNo | rating number of this rating |  |  | mandatory | integer |
| Rating Value XformerWindingRatingValue | value of this rating for this winding | as defined by rating data |  | mandatory | real |
| Rated Voltage XformerWindingRatedVoltage | voltage used in calculating the rating | KV | defaults to base voltage of bus to which winding is connected |  | real |

Transformer TCUL Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Transformer Number XformerNumber | Unique Number representing transformer |  |  |  | integer |
| Winding Bus Identifier XformerWindingBusNo | number of Bus (BusNumber) to which this winding is connected |  |  | mandatory, Must match a bus for A,B,C,or D windiing for TransformerNumber | integer |
| Number of Tap Positions XformerTCULNumberTapPositions | number of tap positions available for TCUL operation in this winding or zero if turns ratio is to be assumed to be continuously variable |  | defaults to zero | must be nonzero for stepwise control | integer |
| Minimum TCUL Adjustment Ratio XformerTCULMinAdjRatio | minimum factor by which TCUL action multiplies winding manually adjusted tap voltage on open circuit | per unit |  | mandatory for TCUL | real |
| Maximum TCUL Adjustment Ratio XformerTCULMaxAdjRatio | maximum factor by which TCUL action multiplies winding manually adjusted tap voltage on open circuit | per unit |  | mandatory for TCUL | real |
| Actual TCUL Adjustment Ratio XformerTCULActualAdjRatio | TCUL adjustment ratio which in conjunction with manually set tap voltage produced voltages voltage magnidue and angles phase angle at terminal buses if case is solved; starting value if case is not solved | per unit |  | mandatory; must correspond to a tap position unless number of tap positions is zero | real |

Transformer TCUL Data (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Control Mode XformerTCULControlMode | Defines control objective to be used in changing this tap NONE = TCUL action disabled VOLT = hold voltage at designated bus between control limits lower voltage limits and upper voltage limits MVAR = hold MVAR flow between designated buses within control limits lower MVAR flow limit and upper MVAR flow limit as measured at "from" bus -controlled element bus 1 flowing into branch or transformer |  | defaults to NONE |  | integer |
| Controlled Element Bus XformerTCULControlBusNo | defines bus at which voltage is to be held within control limits if XformerTCUL ControlMode is VOLT or defines bus into which MVAR flow is controlled if control mode is MVAR. |  |  |  | integer |
| Controlled Element number XformerTCULControlElementNo | Defines line (LineNumber) or transformer (XformerNumber) in which Mvar Flow is controlled when XformerTCUL ControlMode is Mvar |  |  | mandatory if XformerTCUL ControlMode is Mvar | integer |
| Identifier of Controlled Branch or Transformer XformerTCULControlElementType | Element type LINE or XFORMER which Mvarflow is controlled |  |  | mandatory if XformerTCUL ControlMode is Mvar | Text |

Transformer TCUL Data (Continued)

| Name | Description | Units | Default | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Lower MVAR Flow Limit XformerTCULLowerMvarLimit | Minimum desired MVAR flow XformerTCUL ControlMode is Mvar. Positive value indicates flow from controlled element From Bus to controlled element To Bus. | MVAR |  | mandatory if XformerTCUL ControlMode is Mvar lower MVAR flow limit < Upper MVAR flow limit | real |
| Upper MVAR Flow Limit XformerTCULUpperMvarLimit | Maximum desired MVAR flow XformerTCUL ControlMode is Mvar. Positive value indicates flow from controlled element From Bus to controlled element To Bus. | MVAR |  | mandatory if XformerTCUL ControlMode is Mvar lower MVAR flow limit < Upper MVAR flow limit | real |
| Tap Ratio (1...N) XformerTCULTapRatioValue | tap ratio value as abscissa of curve of impedance correction factor versus tap ratio |  | defaults to XformerActual TCUL Adjustment Ratio | monotonically increasing order | real |
| Impedance Adjustment Factor (1...N) XformerTCULImpAdjFactorValue | factor by which total leakage impedance Resistance from winding A to B and Reactance winding A to B of transformer must be multiplied to produce actual winding leakage reactance |  | defaults to unity | valid only for two winding transformer model must be unity if winding C is nonzero | real |

Transformer Manually Adjusted Phase Shift Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Transformer Number XformerNumber | Unique Number representing transformer |  |  |  | integer |
| Winding Bus Identifier XformerWindingBusNo | number of Bus (BusNumber) to which this winding is connected |  |  | mandatory, Must match a bus for A,B,C,or D windiing for TransformerNumber | integer |
| Actual Manually Set Phase Angle XformerManualPhAngAct | actual manually set phase of o.c. voltage of this winding relative to implied reference for this transformer; positive phase increment will decrease flow into this winding | degrees | defaults to zero |  | real |
| Permissible Manually Set Phase Angles (1...n) XformerManualPhAngPermissible | the set of permissible manually set phase angles of o.c. voltage relative to implied reference for the transformer | degrees | defaults to value of actual manual set phase angle | one member of the set must be actual manual set phase angel monotonically increasing order | real |
| Impedance Adjustment Factor (1...n) XformerManualPhAngImpedAdjFact | factor by which total leakage impedance Resistance windinga A to B and Reactance winding A to B of transformer is multiplied for this manually set phase angle |  | defaults to unity | valid only for two winding transformer models must be unity if C winding is non-zero | real |

Transformer Automatically Adjusted Phase Shift Data

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Transformer Number XformerNumber | Unique Number representing transformer |  |  |  | integer |
| Winding Bus Identifier XformerWindingBusNo | number of Bus (BusNumber) to which this winding is connected |  |  | mandatory, Must match a bus for A,B,C,or D windiing for TransformerNumber | integer |
| Number of Automatically Adjustable Phase Shift Positions XformerAutoAdjPhAngNoPos | number of automatically adjustable positions available for phase shifter operation in this winding or zero if phase shift is to be assumed to be continuously variable. |  | defaults to zero | must be nonzero for stepwise control | integer |
| Minimum Automatically Adjustable Phase Shift Angle XformerAutoAdjPhAngMin | minimum automatically adjustable phase shift angle | degrees |  | mandatory; Minimum Automatically Adjustable Phase Shift Angle < Maximum Automatically Adjustable Phase Shift Angle | real |
| Maximum Automatically Adjustable Phase Shift Angle XformerAutoAdjPhAngMax | maximum automatically adjustable phase shift angle | degrees |  | mandatory; same as Minimum Automatically Adjustable Phase Shift Angle | real |
| Actual Automatically Adjusted Phase Shift XformerAutoAdjPhAngAct | automatically adjusted phase shift which when added to manually set phase-actual manual phase set angle produced voltages voltage magnitude and angles voltage phase angleat terminal buses if case is solved; starting value if case is not solved. | degrees |  | mandatory; must correspond to an automatically adjustable phase shift position unless number of automatically adjustable phase set positions is zero | real |

Transformer Automatically Adjusted Phase Shift Data (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Control Mode XformerAutoAdjPhAngCntrlMode | defines control objective to be used in adjusting this phase shift: NONE = phase shift adjustment disabled MW = hold MW flow between designated buses within control limits Lower MW flow limit and Upper MW flow limit as measured at "from" winding bus flowing into line or transformer |  | defaults to NONE |  | integer |
| Controlled Element number XformerAutoAdjPhAngCntrlElNo | Defines line (LineNumber) or transformer (XformerNumber) in which Mw Flow is controlled when XformerAutoAdjPhAngCntrlModeis MW |  |  | mandatory if XformerAutoAdjPhAngContrMode is MW | integer |
| Identifier of Controlled Branch or Transformer XformerAutoAdjPhAngCntrlElType | Device type LINE or XFORMER in which Mw flow is controlled |  |  | mandatory if XformerAutoAdjPhAngContrMode is MW | Text |
| Lower MW Flow Limit XformerAutoAdjPhLowMWLimit | minimum desired MW where flow from controlled element From Bus to controlled element To Bus is positive | MW |  | mandatory if XformerAutoAdjPhAngContrMode is MW; lower MW flow limit < upper MW flow limit | real |
| Upper MW Flow Limit XformerAutoAdjPhHighMWLimit | desired MW where flow from controlled element From Bus to controlled element To Bus is positive | MW |  | mandatory if XformerAutoAdjPhAngContrMode is MW; lower MW flow limit < Upper MW flow limit | real |

Transformer Automatically Adjusted Phase Shift Data (Continued)

| Name | Description | Units | Defaults | Constraints | Data Type |
| --- | --- | --- | --- | --- | --- |
| Automatically Adjustable Phase Shift Angle (1...n) XformerAutoAdjPhAngValue | automatically adjustable phase shift angle value as abscissa of curve of impedance correction factor versus angle | degrees | defaults to XformerActAuto AdjPhAng | monotonically increasing order | real |
| Impedance Adjustment Factor (1...n) XformerAutoAdjPhImpedFactor | factor by which total leakage impedance resistance winding A to B and reactance winding A to B of transformer must be multiplied to produce actual winding leakage impedance |  | defaults to unity | valid only for 2 winding transformers; must be unity if winding C is non-zero | real |