Table 12 - Branch Data

ID#	=  Branch identifier.

Inter area branches are indicated by double letter ID.

Circuits on a common tower have hyphenated ID#.

p	=  Permanent Outage Rate (outages/year).

Dur	=  Permanent Outage Duration (Hours).

t	=  Transient Outage Rate (outages/year).

Con =  Continuous rating.

LTE =  Long-time emergency rating (24 hour).

STE =  Short-time emergency rating (15 minute).

Tr	 =  Transformer off-nominal ratio.

Transformer branches are indicated by Tr  0.

ID		From   To	     L	- Perm -		Tran.	   R		   X		   B	Con	LTE	STE	Tr

#		Bus    Bus	  miles	p	Dur	  t		   pu	  pu       pu	MVA	MVA	MVA	pu

--------------------------------------------------------------------------------------------------------------------------------------

A1		101	102		 3	.24	 16		0.0		0.003	0.014	0.461	175	193	200	0

A2		101	103		55	.51	 10		2.9		0.055	0.211	0.057	175	208	220	0

A3		101	105		22	.33	 10		1.2		0.022	0.085	0.023	175	208	220	0

A4		102	104		33	.39	 10		1.7		0.033	0.127	0.034	175	208	220	0

A5		102	106		50	.48	 10		2.6		0.050	0.192	0.052	175	208	220	0

A6		103	109		31	.38	 10		1.6		0.031	0.119	0.032	175	208	220	0

A7		103	124		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.015

A8		104	109		27	.36	 10		1.4		0.027	0.104	0.028	175	208	220	0

A9		105	110		23	.34	 10		1.2		0.023	0.088	0.024	175	208	220	0

A10		106	110		16	.33	 35		0.0		0.014	0.061	2.459	175	193	200	0

A11		107	108		16	.30	 10		0.8		0.016	0.061	0.017	175	208	220	0

AB1	107	203		42	.44	 10		2.2		0.042	0.161	0.044	175	208	220	0

A12-1	108	109		43	.44	 10		2.3		0.043	0.165	0.045	175	208	220	0

A13-2	108	110		43	.44	 10		2.3		0.043	0.165	0.045	175	208	220	0

A14		109	111		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.03

A15		109	112		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.03

A16		110	111		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.015

A17		110	112		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.015

A18		111	113		33	.40	 11		0.8		0.006	0.048	0.100	500	600	625	0

A19		111	114		29	.39	 11		0.7		0.005	0.042	0.088	500	600	625	0

A20		112	113		33	.40	 11		0.8		0.006	0.048	0.100	500	600	625	0

A21		112	123		67	.52	 11		1.6		0.012	0.097	0.203	500	600	625	0

A22		113	123		60	.49	 11		1.5		0.011	0.087	0.182	500	600	625	0

AB2	113	215		52	.47	 11		1.3		0.010	0.075	0.158	500	600	625	0

A23		114	116		27	.38	 11		0.7		0.005	0.059	0.082	500	600	625	0

A24		115	116		12	.33	 11		0.3		0.002	0.017	0.036	500	600	625	0

A25-1	115	121		34	.41	 11		0.8		0.006	0.049	0.103	500	600	625	0

A25-2	115	121		34	.41	 11		0.8		0.006	0.049	0.103	500	600	625	0

A26		115	124		36	.41	 11		0.9		0.007	0.052	0.109	500	600	625	0

A27		116	117		18	.35	 11		0.4		0.003	0.026	0.055	500	600	625	0

A28		116	119		16	.34	 11		0.4		0.003	0.023	0.049	500	600	625	0

A29		117	118		10	.32	 11		0.2		0.002	0.014	0.030	500	600	625	0

A30		117	122		73	.54	 11		1.8		0.014	0.105	0.221	500	600	625	0

A31-1	118	121		18	.35	 11		0.4		0.003	0.026	0.055	500	600	625	0

A31-2	118	121		18	.35	 11		0.4		0.003	0.026	0.055	500	600	625	0

A32-1	119	120		27.5	.38	 11		0.7		0.005	0.040	0.083	500	600	625	0

A32-2	119	120		27.5	.38	 11		0.7		0.005	0.040	0.083	500	600	625	0

A33-1	120	123		15	.34	 11		0.4		0.003	0.022	0.046	500	600	625	0

A33-2	120	123		15	.34	 11		0.4		0.003	0.022	0.046	500	600	625	0

A34		121	122		47	.45	 11		1.2		0.009	0.068	0.142	500	600	625	0

AB3	123	217		51	.46	 11		1.3		0.010	0.074	0.155	500	600	625	0

B1		201	202		 3	.24	 16		0.0		0.003	0.014	0.461	175	193	200	0

B2		201	203		55	.51	 10		2.9		0.055	0.211	0.057	175	208	220	0

B3		201	205		22	.33	 10		1.2		0.022	0.085	0.023	175	208	220	0

B4		202	204		33	.39	 10		1.7		0.033	0.127	0.034	175	208	220	0

B5		202	206		50	.48	 10		2.6		0.050	0.192	0.052	175	208	220	0

B6		203	209		31	.38	 10		1.6		0.031	0.119	0.032	175	208	220	0

B7		203	224		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.015

B8		204	209		27	.36	 10		1.4		0.027	0.104	0.028	175	208	220	0

B9		205	210		23	.34	 10		1.2		0.023	0.088	0.024	175	208	220	0

B10		206	210		16	.33	 35		0.0		0.014	0.061	2.459	175	193	200	0

B11		207	208		16	.30	 10		0.8		0.016	0.061	0.017	175	208	220	0

B12-1	208	209		43	.44	 10		2.3		0.043	0.165	0.045	175	208	220	0

B13-2	208	210		43	.44	 10		2.3		0.043	0.165	0.045	175	208	220	0

B14		209	211		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.03

B15		209	212		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.03

B16		210	211		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.015

B17		210	212		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.015

B18		211	213		33	.40	 11		0.8		0.006	0.048	0.100	500	600	625	0

B19		211	214		29	.39	 11		0.7		0.005	0.042	0.088	500	600	625	0

B20		212	213		33	.40	 11		0.8		0.006	0.048	0.100	500	600	625	0

B21		212	223		67	.52	 11		1.6		0.012	0.097	0.203	500	600	625	0

B22		213	223		60	.49	 11		1.5		0.011	0.087	0.182	500	600	625	0

B23		214	216		27	.38	 11		0.7		0.005	0.059	0.082	500	600	625	0

B24		215	216		12	.33	 11		0.3		0.002	0.017	0.036	500	600	625	0

B25-1	215	221		34	.41	 11		0.8		0.006	0.049	0.103	500	600	625	0

B25-2	215	221		34	.41	 11		0.8		0.006	0.049	0.103	500	600	625	0

B26		215	224		36	.41	 11		0.9		0.007	0.052	0.109	500	600	625	0

B27		216	217		18	.35	 11		0.4		0.003	0.026	0.055	500	600	625	0

B28		216	219		16	.34	 11		0.4		0.003	0.023	0.049	500	600	625	0

B29		217	218		10	.32	 11		0.2		0.002	0.014	0.030	500	600	625	0

B30		217	222		73	.54	 11		1.8		0.014	0.105	0.221	500	600	625	0

B31-1	218	221		18	.35	 11		0.4		0.003	0.026	0.055	500	600	625	0

B31-2	218	221		18	.35	 11		0.4		0.003	0.026	0.055	500	600	625	0

B32-1	219	220		27.5	.38	 11		0.7		0.005	0.040	0.083	500	600	625	0

B32-2	219	220		27.5	.38	 11		0.7		0.005	0.040	0.083	500	600	625	0

B33-1	220	223		15	.34	 11		0.4		0.003	0.022	0.046	500	600	625	0

B33-2	220	223		15	.34	 11		0.4		0.003	0.022	0.046	500	600	625	0

B34		221	222		47	.45	 11		1.2		0.009	0.068	0.142	500	600	625	0

C1		301	302		 3	.24	 16		0.0		0.003	0.014	0.461	175	193	200	0

C2		301	303		55	.51	 10		2.9		0.055	0.211	0.057	175	208	220	0

C3		301	305		22	.33	 10		1.2		0.022	0.085	0.023	175	208	220	0

C4		302	304		33	.39	 10		1.7		0.033	0.127	0.034	175	208	220	0

C5		302	306		50	.48	 10		2.6		0.050	0.192	0.052	175	208	220	0

C6		303	309		31	.38	 10		1.6		0.031	0.119	0.032	175	208	220	0

C7		303	324		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.015

C8		304	309		27	.36	 10		1.4		0.027	0.104	0.028	175	208	220	0

C9		305	310		23	.34	 10		1.2		0.023	0.088	0.024	175	208	220	0

C10		306	310		16	.33	 35		0.0		0.014	0.061	2.459	175	193	200	0

C11		307	308		16	.30	 10		0.8		0.016	0.061	0.017	175	208	220	0

C12-1	308	309		43	.44	 10		2.3		0.043	0.165	0.045	175	208	220	0

C13-2	308	310		43	.44	 10		2.3		0.043	0.165	0.045	175	208	220	0

C14		309	311		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.03

C15		309	312		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.03

C16		310	311		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.015

C17		310	312		 0	.02	768	0.0		0.002	0.084	0	400	510	600	1.015

C18		311	313		33	.40	 11		0.8		0.006	0.048	0.100	500	600	625	0

C19		311	314		29	.39	 11		0.7		0.005	0.042	0.088	500	600	625	0

C20		312	313		33	.40	 11		0.8		0.006	0.048	0.100	500	600	625	0

C21		312	323		67	.52	 11		1.6		0.012	0.097	0.203	500	600	625	0

C22		313	323		60	.49	 11		1.5		0.011	0.087	0.182	500	600	625	0

C23		314	316		27	.38	 11		0.7		0.005	0.059	0.082	500	600	625	0

C24		315	316		12	.33	 11		0.3		0.002	0.017	0.036	500	600	625	0

C25-1	315	321		34	.41	 11		0.8		0.006	0.049	0.103	500	600	625	0

C25-2	315	321		34	.41	 11		0.8		0.006	0.049	0.103	500	600	625	0

C26		315	324		36	.41	 11		0.9		0.007	0.052	0.109	500	600	625	0

C27		316	317		18	.35	 11		0.4		0.003	0.026	0.055	500	600	625	0

C28		316	319		16	.34	 11		0.4		0.003	0.023	0.049	500	600	625	0

C29		317	318		10	.32	 11		0.2		0.002	0.014	0.030	500	600	625	0

C30		317	322		73	.54	 11		1.8		0.014	0.105	0.221	500	600	625	0

C31-1	318	321		18	.35	 11		0.4		0.003	0.026	0.055	500	600	625	0

C31-2	318	321		18	.35	 11		0.4		0.003	0.026	0.055	500	600	625	0

C32-1	319	320		27.5	.38	 11		0.7		0.005	0.040	0.083	500	600	625	0

C32-2	319	320		27.5	.38	 11		0.7		0.005	0.040	0.083	500	600	625	0

C33-1	320	323		15	.34	 11		0.4		0.003	0.022	0.046	500	600	625	0

C33-2	320	323		15	.34	 11		0.4		0.003	0.022	0.046	500	600	625	0

C34		321	322		47	.45	 11		1.2		0.009	0.068	0.142	500	600	625	0

CA-1	325	121		67	.52	 11		1.6		0.012	0.097	0.203	500	600	625	0

CB-1	318	223		72	.53	 11		1.8		0.013	0.104	0.218	500	600	625	0

C35		323	325		 0	.02	768	0.0		0.000	0.009	0	722	893	893	1.00

The circuits which have common Right-Of-Way (ROW) or Common Structure (CS) are indicated by loops lettered A - G in the one-line diagrams, the common lengths (miles) are as follows:

A - 45 (ROW), B - 15 (CS), C - 18 (CS), D - 34 (ROW), E - 33 (CS), F - 43 (CS), G - 19 (CS).  It is recommended that common mode outages on CS circuits be assigned a frequency of 7.5% of the outage rates presented in table 12; this should be applied for both permanent and transient common mode outages.  The time taken to restore one circuit is the same as the permanent outage duration given in table 12, while the second circuit will take as long again.