Table 13 - Two-Terminal DC Transmission Line Data

(based on reference 3)

Control mode:					Power

DC line resistance ():				5

Power demand (MW):				100

Scheduled DC voltage (kV):			500

Compounding resistance ():			5

Margin in per unit of desired DC power:		0.1

Metered end:					Inverter

Line Outage Rates (Outages/yr): Permanent = 0.22 Transient = 0.7

Permanent Outage Duration (hours):			10

Rectifier	Inverter

Converter bus:					113	316

Number of bridges in series:			4	4

Nominal maximum firing angle:			15	16

Minimum steady state firing angle:			15	16

Commutating transformer resistance/bridge ( ):	0.0180	0.0103

Commutating transformer reactance/bridge ( ):	4.539	4.939

Primary base AC voltage (kV):			230	230

Transformer ratio:					0.46	0.46

Tap setting:					1.15452	0.97987

Max tap setting:					1.15452	1.17500

Min tap setting:					0.97996	0.97987

Rectifier tap step:					0.0050	0.0050

Table 13 (Continued)

The terminal equipment will have the following capacity table:

Capacity (%)		Prob	 (event/yr)	Dur. (hr.)

0    capacity < 50	0.0179	      6.03		 26.00

50  capacity < 75	0.0747	    54.97		 11.90

75  capacity <100	0.0007	      1.08	   	   5.77

Capacity = 100		0.9067	    52.88		150.20